## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-ST-DW-0001-D01 |  |  |  |  | EPC Contractor Tr. No.:BK-HD-PEDCO-T-0100 |  |  | Transmital Date:9/18/2021
Document Title: Standard Drawing For Fire Proofing |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0006-HV-TR-0100 |  |  | Transmital Date:9/18/2021
[5 empty] | CRS No:PEDCO-CRS-BK-GNRAL-PEDCO-000-ST-DW-0001-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Minimum cement content not specified neither in this drawing nor in fireproofing spec Vessels fire proofing details are missed. refer to 1560-00-GEN-CV-SDG-0021 2/2 |  | BK-SUR-ENG-STR-00-01606 | 1400/07/04 | اعمال گردید .
2 | The 100 mm Space is too large. Do you have a reference for this |  | BK-SUR-ENG-STR-00-01606 | 1400/07/04 | فواصل مورد اشاره درالزامات مدرک Passive Fire Protection Specification ارائه شده است. لازم به ذکر است که مدرک فوق AFD می باشد .
3 | ?Is this material safe to use |  | BK-SUR-ENG-STR-00-01606 | 1400/07/04 | مصالح مورد اشاره به دلیل ممنوعیت استفاده (آزبست) حذف گردید . لازم به ذکر است که در دیتیل های شماره 13 الی 18 ، شیوه Fireproof کردن کلیه المانهای سازه ای موجود می باشد .
4 | Compressive Strenght of Concreteis 25 Mpa |  | BK-SUR-ENG-STR-00-01606 | 1400/07/04 | مقاومت فشاری مورد نیاز بتن جهت استفاده در پوشش های ضدحریق منطبق با مدرک Specification For Concrete Work و کافی می باشد .
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: