## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
ELECTRICAL POWER & CONTROL CABLE LIST OF WELL PADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 9
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | EL | LI | 0002 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL POWER & CONTROL CABLE LIST OF WELL PADS نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | May.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-707419
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
ELECTRICAL POWER & CONTROL CABLE LIST OF WELL PADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 9
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 | EL | LI | 0002 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 51
2 | X | [7 empty] | 52
3 | X | [7 empty] | 53
4 | X | [7 empty] | 54
5 | X | [7 empty] | 55
6 | X | [7 empty] | 56
7 | X | [7 empty] | 57
8 | X | [7 empty] | 58
9 | X | [7 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## LEGEND
1. ELECTRICAL CABLE NUMBERING SYSTEM
XXX-XXXXX- XX- XX 1 2 3
(1) 1ST GROUP (EQUIPMENT NUMBER)
(2) 2ND GROUP (CABLE TYPE COMMODITY CODE):
HP: HIGH VOLTAGE POWER CABLE (20 KV & ABOVE)
MP: MEDIUM VOLTAGE POWER CABLE (6 KV & ABOVE)
LP: LOW VOLTAGE POWER CABLE (VOLTAGE LESS THAN 1KV)
SH: CABLE FOR MOTOR SPACE HEATER
CS: CABLE FOR LOCAL CONTROL STATION
CT: CURRENT CABLES
C: CONTROL CABLES
(3) SERIAL NO.
2. CABLE TYPE
MV Power Cables (Armoured) | LV Power Cables | Control Cables
(a) Cable Voltage | (a) Armour Type | (b) Armour Type
M1 11 kV | A Armoured | A Armoured
M2 3.3 kV | U Un-Armoured | U Un-Armoured
(b) Lead Cover Type | (b) Lead Cover type | (c) Lead Cover type
L With Lead cover | L With Lead cover | L With Lead cover
N Without Lead cover | N Without Lead cover | N Without Lead cover
(c) Number of Cores | (c) Number of cores | (d) Number of cores
1 Single Core | 1 to 5 | 1 to 30
3 Multi Core | (d) VFD Type
V VFD Cables
None None VFD Cables
Notes
1- The control cable of IRP Pump will be supplied by vendor
Reference documents are as below:
Area Electrical Cable Route & Section Layout of Well Pads (BK-SSGRL-PEDCO-110-EL-PY-0006)
Electrical Cable Route & Section Layout For Switchgear Building of Well Pads (BK-SSGRL-PEDCO-110-EL-PY-0007)
تسهیلات
ELECTRICAL POWER & CONTROL CABLE LIST OF WELL PADS
شماره صفحه: 3 از 9
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
فعالیت های رو زمینی در بسته های کاری تحت الارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
110
EL
LI
0002
D00
بسته کاری
SSGRL
پروژه
BK

## BK-05
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size (mm2) | Cable Size (SQMM) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | Route
|  |  |  | From | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D00 | TR-001-MP-01 | 11 | Gantry from OHL | WELL05-TR-001 | 200 | 3×50 | 3C | 50 | - | - | 50 | - | - | 33.3 | M1N3 | to Primary Side of Transformer | 01S
2 | D00 | NSWG-001A-LP-A1 | 0.4 | WELL05-TR-001 | WELL05-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
3 | D00 | NSWG-001A-LP-B1 | 0.4 | WELL05-TR-001 | WELL05-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
4 | D00 | NSWG-001A-LP-C1 | 0.4 | WELL05-TR-001 | WELL05-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
5 | D00 | NSWG-001A-LP-N1 | 0.4 | WELL05-TR-001 | WELL05-400-NSWG-001A | 200 | 1×95 | 1C | - | 95 | - | 10 | - | M25 | 23.3 | LAN3 | from Neutral of Transformer to Switchgear | 02S\03S
6 | D00 | NSWG-001A-C-01 | 0.11 VDC | WELL05-TR-001 | WELL05-400-NSWG-001A | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 23.5 | CAN12 | Transformer Mechanical Alarm & Trip to SWG | 02S\03S
7 | D00 | DG-LP-01-A1 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
8 | D00 | DG-LP-01-B1 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
9 | D00 | DG-LP-01-C1 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
10 | D00 | DG-LP-01-A2 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
11 | D00 | DG-LP-01-B2 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
12 | D00 | DG-LP-01-C2 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
13 | D00 | DG-LP-01-A3 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
14 | D00 | DG-LP-01-B3 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
15 | D00 | DG-LP-01-C3 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
16 | D00 | DG-LP-01-N1 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 |  | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
17 | D00 | DG-LP-01-N2 | 0.4 | WELL05-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
18 | D00 | DG-C-01 | 0.11 VDC | WELL05-400-NSWG-001A | Generator Control Panel | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | to Generator Control Panel | 04S\10S\01\03\04
19 | D00 | CB-LP-01 | 0.4 | WELL05-400-NSWG-001A | Capacitor Bank | 50kvar | 3×50 | 4C | 50 | 25 | - | 10 | M40 | M40 | 36.3 | LAN4 | Capacitor Bank | 05S\06S
20 | D00 | IRP-LP-01 | 0.4 | WELL05-400-NSWG-001A | VFD | 90 | 3×185 | 3C | 185 | - | - | 15 | M63 | M63 | 56.9 | LAN3 | Electrical Submersible Pump & Equipment | 05S\06S\07S
21 | D00 | IRP-LP-02 | 0.4 | VFD | IRP Pump | 90 | 3×185 | 3C | 185 | - | - | 100 | M63 | M63 | 56.9 | LAL3V | Electrical Submersible Pump & Equipment | 07S\06S\05S\04S\10S\01\03\05\07\11\12
22 | D00 | 110-CHG-001-LP-01 | 0.4 | WELL05-400-NSWG-001A | WELL05-110-CHG-001 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 1 | 05S\11S
23 | D00 | FB 1-LP-01 | 0.11 VDC | WELL052-110-CHG-001 | Fuse Box 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box 1 | 05S\11S
24 | D00 | BAT 1-LP-01 | 0.11 VDC | Fuse Box 1 | Battery Bank 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank 1 | 05S\11S
25 | D00 | 110-CHG-002-LP-01 | 0.4 | WELL05-400-NSWG-001A | WELL05-110-CHG-002 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 2 | 05S\11S
26 | D00 | FB 1-LP-02 | 0.11 VDC | WELL05-110-CHG-002 | Fuse Box 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box-2 | 05S\11S
27 | D00 | BAT 1-LP-02 | 0.11 VDC | Fuse Box 2 | Battery Bank 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank-2 | 05S\11S
28 | D00 | DP01-LP-01 | 0.4 | WELL05-400-NSWG-001A | WELL05-DP01 | 14.1 | 4×10 | 4C | 10 | 10 | - | 10 | M25 | M25 | 22.1 | LAN4 | Distribution Panel for Switchgear Building | 04S
29 | D00 | DP02-LP-01 | 0.4 | WELL05-400-NSWG-001A | WELL05-DP02 | 6.8 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Security Building | 04S\10S\01\02
30 | D00 | DP03-LP-01 | 0.4 | WELL05-400-NSWG-001A | WELL05-DP03 | 6.4 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Outdoor Area | 04S
31 | D00 | JB-LT-01-LP-01 | 0.4 | WELL05-DP03 | JB-LT-01 | 3.2 | 4×10 | 4C | 10 | 10 | - | 65 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 1 | 04S\01\03\05\06
32 | D00 | JB-LP-02-LP-02 | 0.4 | JB-LP-01 | JB-LP-02 | 3.2 | 4×10 | 4C | 10 | 10 | - | 75 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 2 | 06\07\11\13
33 | D00 | JB-LP-03-LP-03 | 0.4 | WELL05-DP03 | JB-LP-03 | 3.2 | 4×16 | 4C | 16 | 16 | - | 130 | M25 | M25 | 24.5 | LAN4 | Lighting Tower 3 | 04S\10S\01\03\05\07\08
34 | D00 | JB-LP-04-LP-04 | 0.4 | JB-LP-03 | JB-LP-04 | 3.2 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Lighting Tower 4 | 09\10
35 | D00 | WS01-LP-01 | 0.4 | WELL05-400-NSWG-001A | WELL05-WS01 | 37 | 3×70 | 4C | 35 | 35 | - | 95 | M50 | M50 | 41.6 | LAN4 | Welding Socket 1 | 04S\10S\01\03\05\07\11\13\14
36 | D00 | WS01-LP-02 | 0.4 | WELL05-WS01 | WELL05-WS02 | 37 | 3×70 | 4C | 35 | 35 | - | 115 | M50 | M50 | 41.6 | LAN4 | Welding Socket 2 | 13\11\08\09

## BK-12
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size (mm2) | Cable Size (SQMM) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | Route
|  |  |  | From | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D00 | TR-001-MP-01 | 11 | Gantry from OHL | WELL12-TR-001 | 200 | 3×50 | 3C | 50 | - | - | 50 | - | - | 33.3 | M1N3 | to Primary Side of Transformer | 01S
2 | D00 | NSWG-001A-LP-A1 | 0.4 | WELL12-TR-001 | WELL12-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
3 | D00 | NSWG-001A-LP-B1 | 0.4 | WELL12-TR-001 | WELL12-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
4 | D00 | NSWG-001A-LP-C1 | 0.4 | WELL12-TR-001 | WELL12-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
5 | D00 | NSWG-001A-LP-N1 | 0.4 | WELL12-TR-001 | WELL12-400-NSWG-001A | 200 | 1×95 | 1C | - | 95 | - | 10 | - | M25 | 23.3 | LAN3 | from Neutral of Transformer to Switchgear | 02S\03S
6 | D00 | NSWG-001A-C-01 | 0.11 VDC | WELL12-TR-001 | WELL12-400-NSWG-001A | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 23.5 | CAN12 | Transformer Mechanical Alarm & Trip to SWG | 02S\03S
7 | D00 | DG-LP-01-A1 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
8 | D00 | DG-LP-01-B1 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
9 | D00 | DG-LP-01-C1 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
10 | D00 | DG-LP-01-A2 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
11 | D00 | DG-LP-01-B2 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
12 | D00 | DG-LP-01-C2 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
13 | D00 | DG-LP-01-A3 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
14 | D00 | DG-LP-01-B3 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
15 | D00 | DG-LP-01-C3 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
16 | D00 | DG-LP-01-N1 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 |  | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
17 | D00 | DG-LP-01-N2 | 0.4 | WELL12-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
18 | D00 | DG-C-01 | 0.11 VDC | WELL12-400-NSWG-001A | Generator Control Panel | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | to Generator Control Panel | 04S\10S\01\03\04
19 | D00 | CB-LP-01 | 0.4 | WELL12-400-NSWG-001A | Capacitor Bank | 50kvar | 3×50 | 4C | 50 | 25 | - | 10 | M40 | M40 | 36.3 | LAN4 | Capacitor Bank | 05S\06S
20 | D00 | IRP-LP-01 | 0.4 | WELL12-400-NSWG-001A | VFD | 90 | 3×185 | 3C | 185 | - | - | 15 | M63 | M63 | 56.9 | LAN3 | Electrical Submersible Pump & Equipment | 05S\06S\07S
21 | D00 | IRP-LP-02 | 0.4 | VFD | IRP Pump | 90 | 3×185 | 3C | 185 | - | - | 100 | M63 | M63 | 56.9 | LAL3V | Electrical Submersible Pump & Equipment | 07S\06S\05S\04S\10S\01\03\05\07\11\12
22 | D00 | 110-CHG-001-LP-01 | 0.4 | WELL12-400-NSWG-001A | WELL12-110-CHG-001 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 1 | 05S\11S
23 | D00 | FB 1-LP-01 | 0.11 VDC | WELL122-110-CHG-001 | Fuse Box 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box 1 | 05S\11S
24 | D00 | BAT 1-LP-01 | 0.11 VDC | Fuse Box 1 | Battery Bank 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank 1 | 05S\11S
25 | D00 | 110-CHG-002-LP-01 | 0.4 | WELL12-400-NSWG-001A | WELL12-110-CHG-002 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 2 | 05S\11S
26 | D00 | FB 1-LP-02 | 0.11 VDC | WELL12-110-CHG-002 | Fuse Box 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box-2 | 05S\11S
27 | D00 | BAT 1-LP-02 | 0.11 VDC | Fuse Box 2 | Battery Bank 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank-2 | 05S\11S
28 | D00 | DP01-LP-01 | 0.4 | WELL12-400-NSWG-001A | WELL12-DP01 | 14.1 | 4×10 | 4C | 10 | 10 | - | 10 | M25 | M25 | 22.1 | LAN4 | Distribution Panel for Switchgear Building | 04S
29 | D00 | DP02-LP-01 | 0.4 | WELL12-400-NSWG-001A | WELL12-DP02 | 6.8 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Security Building | 04S\10S\01\02
30 | D00 | DP03-LP-01 | 0.4 | WELL12-400-NSWG-001A | WELL12-DP03 | 6.4 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Outdoor Area | 04S
31 | D00 | JB-LT-01-LP-01 | 0.4 | WELL12-DP03 | JB-LT-01 | 3.2 | 4×10 | 4C | 10 | 10 | - | 65 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 1 | 04S\01\03\05\06
32 | D00 | JB-LP-02-LP-02 | 0.4 | JB-LP-01 | JB-LP-02 | 3.2 | 4×10 | 4C | 10 | 10 | - | 75 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 2 | 06\07\11\13
33 | D00 | JB-LP-03-LP-03 | 0.4 | WELL12-DP03 | JB-LP-03 | 3.2 | 4×16 | 4C | 16 | 16 | - | 130 | M25 | M25 | 24.5 | LAN4 | Lighting Tower 3 | 04S\10S\01\03\05\07\08
34 | D00 | JB-LP-04-LP-04 | 0.4 | JB-LP-03 | JB-LP-04 | 3.2 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Lighting Tower 4 | 09\10
35 | D00 | WS01-LP-01 | 0.4 | WELL12-400-NSWG-001A | WELL12-WS01 | 37 | 3×70 | 4C | 35 | 35 | - | 95 | M50 | M50 | 41.6 | LAN4 | Welding Socket 1 | 04S\10S\01\03\05\07\11\13\14
36 | D00 | WS01-LP-02 | 0.4 | WELL12-WS01 | WELL12-WS02 | 37 | 3×70 | 4C | 35 | 35 | - | 115 | M50 | M50 | 41.6 | LAN4 | Welding Socket 2 | 13\11\08\09

## BK-14
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size (mm2) | Cable Size (SQMM) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | Route
|  |  |  | From | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D00 | TR-001-MP-01 | 11 | Gantry from OHL | WELL14-TR-001 | 200 | 3×50 | 3C | 50 | - | - | 50 | - | - | 33.3 | M1N3 | to Primary Side of Transformer | 01S
2 | D00 | NSWG-001A-LP-A1 | 0.4 | WELL14-TR-001 | WELL14-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
3 | D00 | NSWG-001A-LP-B1 | 0.4 | WELL14-TR-001 | WELL14-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
4 | D00 | NSWG-001A-LP-C1 | 0.4 | WELL14-TR-001 | WELL14-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
5 | D00 | NSWG-001A-LP-N1 | 0.4 | WELL14-TR-001 | WELL14-400-NSWG-001A | 200 | 1×95 | 1C | - | 95 | - | 10 | - | M25 | 23.3 | LAN3 | from Neutral of Transformer to Switchgear | 02S\03S
6 | D00 | NSWG-001A-C-01 | 0.11 VDC | WELL14-TR-001 | WELL14-400-NSWG-001A | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 23.5 | CAN12 | Transformer Mechanical Alarm & Trip to SWG | 02S\03S
7 | D00 | DG-LP-01-A1 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
8 | D00 | DG-LP-01-B1 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
9 | D00 | DG-LP-01-C1 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
10 | D00 | DG-LP-01-A2 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
11 | D00 | DG-LP-01-B2 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
12 | D00 | DG-LP-01-C2 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
13 | D00 | DG-LP-01-A3 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
14 | D00 | DG-LP-01-B3 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
15 | D00 | DG-LP-01-C3 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
16 | D00 | DG-LP-01-N1 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 |  | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
17 | D00 | DG-LP-01-N2 | 0.4 | WELL14-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
18 | D00 | DG-C-01 | 0.11 VDC | WELL14-400-NSWG-001A | Generator Control Panel | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | to Generator Control Panel | 04S\10S\01\03\04
19 | D00 | CB-LP-01 | 0.4 | WELL14-400-NSWG-001A | Capacitor Bank | 50kvar | 3×50 | 4C | 50 | 25 | - | 10 | M40 | M40 | 36.3 | LAN4 | Capacitor Bank | 05S\06S
20 | D00 | IRP-LP-01 | 0.4 | WELL14-400-NSWG-001A | VFD | 90 | 3×185 | 3C | 185 | - | - | 15 | M63 | M63 | 56.9 | LAN3 | Electrical Submersible Pump & Equipment | 05S\06S\07S
21 | D00 | IRP-LP-02 | 0.4 | VFD | IRP Pump | 90 | 3×185 | 3C | 185 | - | - | 100 | M63 | M63 | 56.9 | LAL3V | Electrical Submersible Pump & Equipment | 07S\06S\05S\04S\10S\01\03\05\07\11\12
22 | D00 | 110-CHG-001-LP-01 | 0.4 | WELL14-400-NSWG-001A | WELL14-110-CHG-001 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 1 | 05S\11S
23 | D00 | FB 1-LP-01 | 0.11 VDC | WELL142-110-CHG-001 | Fuse Box 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box 1 | 05S\11S
24 | D00 | BAT 1-LP-01 | 0.11 VDC | Fuse Box 1 | Battery Bank 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank 1 | 05S\11S
25 | D00 | 110-CHG-002-LP-01 | 0.4 | WELL14-400-NSWG-001A | WELL14-110-CHG-002 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 2 | 05S\11S
26 | D00 | FB 1-LP-02 | 0.11 VDC | WELL14-110-CHG-002 | Fuse Box 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box-2 | 05S\11S
27 | D00 | BAT 1-LP-02 | 0.11 VDC | Fuse Box 2 | Battery Bank 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank-2 | 05S\11S
28 | D00 | DP01-LP-01 | 0.4 | WELL14-400-NSWG-001A | WELL14-DP01 | 14.1 | 4×10 | 4C | 10 | 10 | - | 10 | M25 | M25 | 22.1 | LAN4 | Distribution Panel for Switchgear Building | 04S
29 | D00 | DP02-LP-01 | 0.4 | WELL14-400-NSWG-001A | WELL14-DP02 | 6.8 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Security Building | 04S\10S\01\02
30 | D00 | DP03-LP-01 | 0.4 | WELL14-400-NSWG-001A | WELL14-DP03 | 6.4 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Outdoor Area | 04S
31 | D00 | JB-LT-01-LP-01 | 0.4 | WELL14-DP03 | JB-LT-01 | 3.2 | 4×10 | 4C | 10 | 10 | - | 65 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 1 | 04S\01\03\05\06
32 | D00 | JB-LP-02-LP-02 | 0.4 | JB-LP-01 | JB-LP-02 | 3.2 | 4×10 | 4C | 10 | 10 | - | 75 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 2 | 06\07\11\13
33 | D00 | JB-LP-03-LP-03 | 0.4 | WELL14-DP03 | JB-LP-03 | 3.2 | 4×16 | 4C | 16 | 16 | - | 130 | M25 | M25 | 24.5 | LAN4 | Lighting Tower 3 | 04S\10S\01\03\05\07\08
34 | D00 | JB-LP-04-LP-04 | 0.4 | JB-LP-03 | JB-LP-04 | 3.2 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Lighting Tower 4 | 09\10
35 | D00 | WS01-LP-01 | 0.4 | WELL14-400-NSWG-001A | WELL14-WS01 | 37 | 3×70 | 4C | 35 | 35 | - | 95 | M50 | M50 | 41.6 | LAN4 | Welding Socket 1 | 04S\10S\01\03\05\07\11\13\14
36 | D00 | WS01-LP-02 | 0.4 | WELL14-WS01 | WELL14-WS02 | 37 | 3×70 | 4C | 35 | 35 | - | 115 | M50 | M50 | 41.6 | LAN4 | Welding Socket 2 | 13\11\08\09

## BK-15
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size (mm2) | Cable Size (SQMM) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | Route
|  |  |  | From | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D00 | TR-001-MP-01 | 11 | Gantry from OHL | WELL15-TR-001 | 200 | 3×50 | 3C | 50 | - | - | 50 | - | - | 33.3 | M1N3 | to Primary Side of Transformer | 01S
2 | D00 | NSWG-001A-LP-A1 | 0.4 | WELL15-TR-001 | WELL15-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
3 | D00 | NSWG-001A-LP-B1 | 0.4 | WELL15-TR-001 | WELL15-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
4 | D00 | NSWG-001A-LP-C1 | 0.4 | WELL15-TR-001 | WELL15-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
5 | D00 | NSWG-001A-LP-N1 | 0.4 | WELL15-TR-001 | WELL15-400-NSWG-001A | 200 | 1×95 | 1C | - | 95 | - | 10 | - | M25 | 23.3 | LAN3 | from Neutral of Transformer to Switchgear | 02S\03S
6 | D00 | NSWG-001A-C-01 | 0.11 VDC | WELL15-TR-001 | WELL15-400-NSWG-001A | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 23.5 | CAN12 | Transformer Mechanical Alarm & Trip to SWG | 02S\03S
7 | D00 | DG-LP-01-A1 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
8 | D00 | DG-LP-01-B1 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
9 | D00 | DG-LP-01-C1 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
10 | D00 | DG-LP-01-A2 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
11 | D00 | DG-LP-01-B2 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
12 | D00 | DG-LP-01-C2 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
13 | D00 | DG-LP-01-A3 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
14 | D00 | DG-LP-01-B3 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
15 | D00 | DG-LP-01-C3 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
16 | D00 | DG-LP-01-N1 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 |  | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
17 | D00 | DG-LP-01-N2 | 0.4 | WELL15-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
18 | D00 | DG-C-01 | 0.11 VDC | WELL15-400-NSWG-001A | Generator Control Panel | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | to Generator Control Panel | 04S\10S\01\03\04
19 | D00 | CB-LP-01 | 0.4 | WELL15-400-NSWG-001A | Capacitor Bank | 50kvar | 3×50 | 4C | 50 | 25 | - | 10 | M40 | M40 | 36.3 | LAN4 | Capacitor Bank | 05S\06S
20 | D00 | IRP-LP-01 | 0.4 | WELL15-400-NSWG-001A | VFD | 90 | 3×185 | 3C | 185 | - | - | 15 | M63 | M63 | 56.9 | LAN3 | Electrical Submersible Pump & Equipment | 05S\06S\07S
21 | D00 | IRP-LP-02 | 0.4 | VFD | IRP Pump | 90 | 3×185 | 3C | 185 | - | - | 100 | M63 | M63 | 56.9 | LAL3V | Electrical Submersible Pump & Equipment | 07S\06S\05S\04S\10S\01\03\05\07\11\12
22 | D00 | 110-CHG-001-LP-01 | 0.4 | WELL15-400-NSWG-001A | WELL15-110-CHG-001 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 1 | 05S\11S
23 | D00 | FB 1-LP-01 | 0.11 VDC | WELL152-110-CHG-001 | Fuse Box 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box 1 | 05S\11S
24 | D00 | BAT 1-LP-01 | 0.11 VDC | Fuse Box 1 | Battery Bank 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank 1 | 05S\11S
25 | D00 | 110-CHG-002-LP-01 | 0.4 | WELL15-400-NSWG-001A | WELL15-110-CHG-002 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 2 | 05S\11S
26 | D00 | FB 1-LP-02 | 0.11 VDC | WELL15-110-CHG-002 | Fuse Box 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box-2 | 05S\11S
27 | D00 | BAT 1-LP-02 | 0.11 VDC | Fuse Box 2 | Battery Bank 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank-2 | 05S\11S
28 | D00 | DP01-LP-01 | 0.4 | WELL15-400-NSWG-001A | WELL15-DP01 | 14.1 | 4×10 | 4C | 10 | 10 | - | 10 | M25 | M25 | 22.1 | LAN4 | Distribution Panel for Switchgear Building | 04S
29 | D00 | DP02-LP-01 | 0.4 | WELL15-400-NSWG-001A | WELL15-DP02 | 6.8 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Security Building | 04S\10S\01\02
30 | D00 | DP03-LP-01 | 0.4 | WELL15-400-NSWG-001A | WELL15-DP03 | 6.4 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Outdoor Area | 04S
31 | D00 | JB-LT-01-LP-01 | 0.4 | WELL15-DP03 | JB-LT-01 | 3.2 | 4×10 | 4C | 10 | 10 | - | 65 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 1 | 04S\01\03\05\06
32 | D00 | JB-LP-02-LP-02 | 0.4 | JB-LP-01 | JB-LP-02 | 3.2 | 4×10 | 4C | 10 | 10 | - | 75 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 2 | 06\07\11\13
33 | D00 | JB-LP-03-LP-03 | 0.4 | WELL15-DP03 | JB-LP-03 | 3.2 | 4×16 | 4C | 16 | 16 | - | 130 | M25 | M25 | 24.5 | LAN4 | Lighting Tower 3 | 04S\10S\01\03\05\07\08
34 | D00 | JB-LP-04-LP-04 | 0.4 | JB-LP-03 | JB-LP-04 | 3.2 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Lighting Tower 4 | 09\10
35 | D00 | WS01-LP-01 | 0.4 | WELL15-400-NSWG-001A | WELL15-WS01 | 37 | 3×70 | 4C | 35 | 35 | - | 95 | M50 | M50 | 41.6 | LAN4 | Welding Socket 1 | 04S\10S\01\03\05\07\11\13\14
36 | D00 | WS01-LP-02 | 0.4 | WELL15-WS01 | WELL15-WS02 | 37 | 3×70 | 4C | 35 | 35 | - | 115 | M50 | M50 | 41.6 | LAN4 | Welding Socket 2 | 13\11\08\09

## W-007
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size (mm2) | Cable Size (SQMM) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | Route
|  |  |  | From | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D00 | TR-001-MP-01 | 11 | Gantry from OHL | WELL007-TR-001 | 200 | 3×50 | 3C | 50 | - | - | 50 | - | - | 33.3 | M1N3 | to Primary Side of Transformer | 01S
2 | D00 | NSWG-001A-LP-A1 | 0.4 | WELL007-TR-001 | WELL007-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
3 | D00 | NSWG-001A-LP-B1 | 0.4 | WELL007-TR-001 | WELL007-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
4 | D00 | NSWG-001A-LP-C1 | 0.4 | WELL007-TR-001 | WELL007-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
5 | D00 | NSWG-001A-LP-N1 | 0.4 | WELL007-TR-001 | WELL007-400-NSWG-001A | 200 | 1×95 | 1C | - | 95 | - | 10 | - | M25 | 23.3 | LAN3 | from Neutral of Transformer to Switchgear | 02S\03S
6 | D00 | NSWG-001A-C-01 | 0.11 VDC | WELL007-TR-001 | WELL007-400-NSWG-001A | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 23.5 | CAN12 | Transformer Mechanical Alarm & Trip to SWG | 02S\03S
7 | D00 | DG-LP-01-A1 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
8 | D00 | DG-LP-01-B1 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
9 | D00 | DG-LP-01-C1 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
10 | D00 | DG-LP-01-A2 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
11 | D00 | DG-LP-01-B2 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
12 | D00 | DG-LP-01-C2 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
13 | D00 | DG-LP-01-A3 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
14 | D00 | DG-LP-01-B3 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
15 | D00 | DG-LP-01-C3 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
16 | D00 | DG-LP-01-N1 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 |  | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
17 | D00 | DG-LP-01-N2 | 0.4 | WELL007-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
18 | D00 | DG-C-01 | 0.11 VDC | WELL007-400-NSWG-001A | Generator Control Panel | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | to Generator Control Panel | 04S\10S\01\03\04
19 | D00 | CB-LP-01 | 0.4 | WELL007-400-NSWG-001A | Capacitor Bank | 50kvar | 3×50 | 4C | 50 | 25 | - | 10 | M40 | M40 | 36.3 | LAN4 | Capacitor Bank | 05S\06S
20 | D00 | IRP-LP-01 | 0.4 | WELL007-400-NSWG-001A | VFD | 90 | 3×185 | 3C | 185 | - | - | 15 | M63 | M63 | 56.9 | LAN3 | Electrical Submersible Pump & Equipment | 05S\06S\07S
21 | D00 | IRP-LP-02 | 0.4 | VFD | IRP Pump | 90 | 3×185 | 3C | 185 | - | - | 100 | M63 | M63 | 56.9 | LAL3V | Electrical Submersible Pump & Equipment | 07S\06S\05S\04S\10S\01\03\05\07\11\12
22 | D00 | 110-CHG-001-LP-01 | 0.4 | WELL007-400-NSWG-001A | WELL007-110-CHG-001 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 1 | 05S\11S
23 | D00 | FB 1-LP-01 | 0.11 VDC | WELL0072-110-CHG-001 | Fuse Box 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box 1 | 05S\11S
24 | D00 | BAT 1-LP-01 | 0.11 VDC | Fuse Box 1 | Battery Bank 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank 1 | 05S\11S
25 | D00 | 110-CHG-002-LP-01 | 0.4 | WELL007-400-NSWG-001A | WELL007-110-CHG-002 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 2 | 05S\11S
26 | D00 | FB 1-LP-02 | 0.11 VDC | WELL007-110-CHG-002 | Fuse Box 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box-2 | 05S\11S
27 | D00 | BAT 1-LP-02 | 0.11 VDC | Fuse Box 2 | Battery Bank 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank-2 | 05S\11S
28 | D00 | DP01-LP-01 | 0.4 | WELL007-400-NSWG-001A | WELL007-DP01 | 14.1 | 4×10 | 4C | 10 | 10 | - | 10 | M25 | M25 | 22.1 | LAN4 | Distribution Panel for Switchgear Building | 04S
29 | D00 | DP02-LP-01 | 0.4 | WELL007-400-NSWG-001A | WELL007-DP02 | 6.8 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Security Building | 04S\10S\01\02
30 | D00 | DP03-LP-01 | 0.4 | WELL007-400-NSWG-001A | WELL007-DP03 | 6.4 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Outdoor Area | 04S
31 | D00 | JB-LT-01-LP-01 | 0.4 | WELL007-DP03 | JB-LT-01 | 3.2 | 4×10 | 4C | 10 | 10 | - | 65 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 1 | 04S\01\03\05\06
32 | D00 | JB-LP-02-LP-02 | 0.4 | JB-LP-01 | JB-LP-02 | 3.2 | 4×10 | 4C | 10 | 10 | - | 75 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 2 | 06\07\11\13
33 | D00 | JB-LP-03-LP-03 | 0.4 | WELL007-DP03 | JB-LP-03 | 3.2 | 4×16 | 4C | 16 | 16 | - | 130 | M25 | M25 | 24.5 | LAN4 | Lighting Tower 3 | 04S\10S\01\03\05\07\08
34 | D00 | JB-LP-04-LP-04 | 0.4 | JB-LP-03 | JB-LP-04 | 3.2 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Lighting Tower 4 | 09\10
35 | D00 | WS01-LP-01 | 0.4 | WELL007-400-NSWG-001A | WELL007-WS01 | 37 | 3×70 | 4C | 35 | 35 | - | 95 | M50 | M50 | 41.6 | LAN4 | Welding Socket 1 | 04S\10S\01\03\05\07\11\13\14
36 | D00 | WS01-LP-02 | 0.4 | WELL007-WS01 | WELL007-WS02 | 37 | 3×70 | 4C | 35 | 35 | - | 115 | M50 | M50 | 41.6 | LAN4 | Welding Socket 2 | 13\11\08\09

## W-046
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size (mm2) | Cable Size (SQMM) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description | Route
|  |  |  | From | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D00 | TR-001-MP-01 | 11 | Gantry from OHL | WELL046-TR-001 | 200 | 3×50 | 3C | 50 | - | - | 50 | - | - | 33.3 | M1N3 | to Primary Side of Transformer | 01S
2 | D00 | NSWG-001A-LP-A1 | 0.4 | WELL046-TR-001 | WELL046-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
3 | D00 | NSWG-001A-LP-B1 | 0.4 | WELL046-TR-001 | WELL046-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
4 | D00 | NSWG-001A-LP-C1 | 0.4 | WELL046-TR-001 | WELL046-400-NSWG-001A | 200 | 1×185 | 1C | 185 | - | - | 10 | - | M32 | 29 | LAN3 | from Secondary Side of Transformer to Switchgear | 02S\03S
5 | D00 | NSWG-001A-LP-N1 | 0.4 | WELL046-TR-001 | WELL046-400-NSWG-001A | 200 | 1×95 | 1C | - | 95 | - | 10 | - | M25 | 23.3 | LAN3 | from Neutral of Transformer to Switchgear | 02S\03S
6 | D00 | NSWG-001A-C-01 | 0.11 VDC | WELL046-TR-001 | WELL046-400-NSWG-001A | - | 12×2.5 | 12C | 2.5 | - | - | 10 | M25 | M25 | 23.5 | CAN12 | Transformer Mechanical Alarm & Trip to SWG | 02S\03S
7 | D00 | DG-LP-01-A1 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
8 | D00 | DG-LP-01-B1 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
9 | D00 | DG-LP-01-C1 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
10 | D00 | DG-LP-01-A2 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
11 | D00 | DG-LP-01-B2 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
12 | D00 | DG-LP-01-C2 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
13 | D00 | DG-LP-01-A3 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
14 | D00 | DG-LP-01-B3 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
15 | D00 | DG-LP-01-C3 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
16 | D00 | DG-LP-01-N1 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 |  | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
17 | D00 | DG-LP-01-N2 | 0.4 | WELL046-400-NSWG-001A | Generator Control Panel | 200 | 1×185 | 1C | 185 | - | - | 50 | M32 | M32 | 29 | LAN3 | to Generator Control Panel | 04S\10S\01\03\04
18 | D00 | DG-C-01 | 0.11 VDC | WELL046-400-NSWG-001A | Generator Control Panel | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | to Generator Control Panel | 04S\10S\01\03\04
19 | D00 | CB-LP-01 | 0.4 | WELL046-400-NSWG-001A | Capacitor Bank | 50kvar | 3×50 | 4C | 50 | 25 | - | 10 | M40 | M40 | 36.3 | LAN4 | Capacitor Bank | 05S\06S
20 | D00 | IRP-LP-01 | 0.4 | WELL046-400-NSWG-001A | VFD | 90 | 3×185 | 3C | 185 | - | - | 15 | M63 | M63 | 56.9 | LAN3 | Electrical Submersible Pump & Equipment | 05S\06S\07S
21 | D00 | IRP-LP-02 | 0.4 | VFD | IRP Pump | 90 | 3×185 | 3C | 185 | - | - | 100 | M63 | M63 | 56.9 | LAL3V | Electrical Submersible Pump & Equipment | 07S\06S\05S\04S\10S\01\03\05\07\11\12
22 | D00 | 110-CHG-001-LP-01 | 0.4 | WELL046-400-NSWG-001A | WELL046-110-CHG-001 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 1 | 05S\11S
23 | D00 | FB 1-LP-01 | 0.11 VDC | WELL0462-110-CHG-001 | Fuse Box 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box 1 | 05S\11S
24 | D00 | BAT 1-LP-01 | 0.11 VDC | Fuse Box 1 | Battery Bank 1 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank 1 | 05S\11S
25 | D00 | 110-CHG-002-LP-01 | 0.4 | WELL046-400-NSWG-001A | WELL046-110-CHG-002 | 3 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN3 | 110VDC Charger 2 | 05S\11S
26 | D00 | FB 1-LP-02 | 0.11 VDC | WELL046-110-CHG-002 | Fuse Box 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Fuse Box-2 | 05S\11S
27 | D00 | BAT 1-LP-02 | 0.11 VDC | Fuse Box 2 | Battery Bank 2 | - | 2×6 | 2C | 6 | - | - | 10 | M20 | M20 | 16.8 | LAN2 | DC Charger Battery Bank-2 | 05S\11S
28 | D00 | DP01-LP-01 | 0.4 | WELL046-400-NSWG-001A | WELL046-DP01 | 14.1 | 4×10 | 4C | 10 | 10 | - | 10 | M25 | M25 | 22.1 | LAN4 | Distribution Panel for Switchgear Building | 04S
29 | D00 | DP02-LP-01 | 0.4 | WELL046-400-NSWG-001A | WELL046-DP02 | 6.8 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Security Building | 04S\10S\01\02
30 | D00 | DP03-LP-01 | 0.4 | WELL046-400-NSWG-001A | WELL046-DP03 | 6.4 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Distribution Panel for Outdoor Area | 04S
31 | D00 | JB-LT-01-LP-01 | 0.4 | WELL046-DP03 | JB-LT-01 | 3.2 | 4×10 | 4C | 10 | 10 | - | 65 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 1 | 04S\01\03\05\06
32 | D00 | JB-LP-02-LP-02 | 0.4 | JB-LP-01 | JB-LP-02 | 3.2 | 4×10 | 4C | 10 | 10 | - | 75 | M25 | M25 | 22.1 | LAN4 | Lighting Tower 2 | 06\07\11\13
33 | D00 | JB-LP-03-LP-03 | 0.4 | WELL046-DP03 | JB-LP-03 | 3.2 | 4×16 | 4C | 16 | 16 | - | 130 | M25 | M25 | 24.5 | LAN4 | Lighting Tower 3 | 04S\10S\01\03\05\07\08
34 | D00 | JB-LP-04-LP-04 | 0.4 | JB-LP-03 | JB-LP-04 | 3.2 | 4×6 | 4C | 6 | 6 | - | 10 | M25 | M25 | 19.7 | LAN4 | Lighting Tower 4 | 09\10
35 | D00 | WS01-LP-01 | 0.4 | WELL046-400-NSWG-001A | WELL046-WS01 | 37 | 3×70 | 4C | 35 | 35 | - | 95 | M50 | M50 | 41.6 | LAN4 | Welding Socket 1 | 04S\10S\01\03\05\07\11\13\14
36 | D00 | WS01-LP-02 | 0.4 | WELL046-WS01 | WELL046-WS02 | 37 | 3×70 | 4C | 35 | 35 | - | 115 | M50 | M50 | 41.6 | LAN4 | Welding Socket 2 | 13\11\08\09