## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-000-ST-DW-0017 |  |  |  |  | EPC Contractor Tr. No.:BK-HD-PEDCO-T-0625 |  |  | Transmital Date:02/22/2022
Document Title: Standard Derawing For Septic Tank |  |  |  |  | PEDCO Tr. No.:BK-PEDCO-NISOC-0005-ST-TR-0625 |  |  | Transmital Date:02/22/2022
[5 empty] | CRS No:NISOC-CRS-BK-GNRAL-PEDCO-000-ST-DW-0017_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 |  |  | MB-SUR-ENG-STR-00-03355 | 2022-05-24 | به منظور شستشو و استفاده از پمپ کفکش این چاله هادر نظرگرفته شده است
2 |  |  | MB-SUR-ENG-STR-00-03355 | 2022-05-24 | با عنایت به نظر کارفرمای محترم ، دیواربتنی به همراه واتراستاپ در محل اتصال دیوار به کف و عایق امولسیونی بر روی بتن دیوار و فونداسیون در مجاورت خاک ، جایگزین طرح قبلی گردید.
3 |  |  | MB-SUR-ENG-STR-00-03355 | 2022-05-24 | باتوجه به ذخیره فاضلاب ، در صورت استفاده از ladder امکان لغزنده شدن سطح آن و غیر ایمن شدن وجود دارد و بهتر است در زمان ورود به داخل مخزن از پله پرتابل استفاده گردد.در صورت امکان بدلیل سهولت در اجرا و همچنین برداشتن دریچه توسط بهره بردار با دیتایل Chequred Plate موافقت فرمایید. به نظر میرسد با توجه به کاربری سازه فوق نیازی به آببند بودن دریچه نمی باشد.
4 |  |  | MB-SUR-ENG-STR-00-03355 | 2022-05-24 | ارتفاع به جهت جلوگیری از فشار زیر سقف در زمان پرشدن مخزن در نظر گرفته شده است که به تبع آن احجام بیشتر از مقادیر خواسته شده در نظر گرفته شده است.مقادیر ستون نشان داده شده برابر است با مجموع پارامترهای D و E منهای تراز بالای سقف از زمین پیرامون.
Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Legend
| CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
Signature | Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: