## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0009_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0563 |  |  | Transmital Date: 08-Feb-2022
Document Title: Data Sheets For MV Induction Motors |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-EL-TR-0563 |  |  | Transmital Date: 08-Feb-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DT-0009_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | کلیه ایتم های این مدرک می بایست براساس الزامات استاندارد IPS-M-EL-132(2) تکمیل گردد. به عنوان مثال آیتم 17،که بخش Brazed copper می بایست علامت زده شود. |  | 1400-2294-424217 | 1400-12-05 | بندهای IPS-M-EL-132 مورد بررسی قرار گرفت و این دیتاشیت بر اساس آن به روزرسانی گردید. همچنین آیتم Rotor Construction اصلاح شد.
2 | صفحه 6/7 آیتم 84 برای الکترومتورهای زیر 500KW در بخش تست های روتین Witness در نظر گرفته شود ،ضمنا شرایط تست در ITP سازنده نهایی خواهد شد. |  | 1400-2294-424217 | 1400-12-05 | اعمال گردید.
3 | لازم است که مدرک براساس استاندارد شماره گذاری مناطق نفتخیز جنوب شماره گذاری شود. |  | 1400-2294-424217 | 1400-12-05 | مدرک بر اساس استاندارد شماره گذاری شده و مورد توافق در MDL پروژه نام گذاری شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 19-Feb-22 |  |  |  |  | Date: