## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0008_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0558 |  |  | Transmital Date: 07-Feb-2022
Document Title: Data Sheets For LV Induction Motors |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-EL-TR-0558 |  |  | Transmital Date: 07-Feb-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DT-0008_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This data sheet shall be in rechecked with data sheet attached to IPS-M-EL-131(2) and all data which are exist in IPS data sheet shall be exist in the project data sheet. |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | تمامی اطلاعات اشاره شده در استاندارد IPS-M-EL-131 ویرایش دوم در این مدرک لحاظ شده است. |  |  | See below item 5.
2 | Part B, Item1: According to "Electrical System Design Criteria" voltage and frequency variation shall be modified to ± 10% and ± 5%. |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | اعمال گردید |  |  | Noted and closed.
3 | Part B, Item13: According to "Electrical System Design Criteria" temperature rise shall be considered "B". |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | اعمال گردید |  |  | Noted and closed.
4 | Part B, Item 21: According to "Electrical System Design Criteria" shall be modified to 85 dB @ 1 m |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | اعمال گردید |  |  | Noted and closed.
5 | Ref. Item 1 above: Despite the consultant's response some rows in attached data sheet of IPS-M-EL-131(2), such as gas group, temperature class, No load losses and etc not been added to Data Sheets For LV Induction Motors. For more guidance, use attached data sheet that has been submitted to consultant on 9/Jan/2022. |  | BK-SUR-ENG-ELE-00-03090 | 2022-02-19 | مدرک نمونه مورد بررسی قرار گرفت و موارد جامانده، در این مدرک لحاظ گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 19-Feb-22 |  |  |  |  | Date: