## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0009_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0563 |  |  | Transmital Date: 08-Feb-2022
Document Title: Data Sheets For MV Induction Motors |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-EL-TR-0563 |  |  | Transmital Date: 08-Feb-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DT-0009_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This data sheet shall be in rechecked with data sheet attached to IPS-M-EL-132(2) and all data which are exist in IPS data sheet shall be exist in the project data sheet. |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | داده برگه بر اساس فایل الکترونیکی دریافتی از کارفرمای محترم طی نامه شماره 213958 به روز رسانی گردید. |  |  | Noted and Closed.
2 | Part B, Item 1: According to "Electrical System Design Criteria" voltage and frequency variation shall be modified to ± 10% and ± 5%. |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | ولتاژ موتورهای MV به 11 و 3.3 کیلوولت تغییر پیدا کرد. |  |  | Noted and Closed.
3 | Part B, Item 21: According to "Electrical System Design Criteria" item 21 part B shall be modified to 85 dB @ 1 m |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | اعمال گردید |  |  | Noted and Closed.
4 | Part B, Item 30: According to "Electrical System Design Criteria" RTD shall be considered for stator winding of MV motors. (3 RTD for each phase) |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | RTD مطابق با استاندارد IPS برای موتورهای MV در نظر گرفته شده است. |  |  | Noted and Closed.
5 | Part B, Item 28: Diffrential protection is required for motors with rated power 1000kW and above. Diffrential protection Scheme (self balancing / Conventional) shall be determined by consultant. Self balancing is prefered due to less cost, less required space and less unwanted false trips. |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | به صورت نوت شماره 2 اضافه گردید. |  |  | See below item 8.
6 | Part B, Item 28 and 29: in case of selecting self balaning scheme, CTs shall be provided by motor Manufacturer and installed in the motor terminal box. And special care shall be considered on CT window size and motor cables overall diameter to be coordinate with each other. |  | BK-SSR-ENG-ELE-00-01560 | 2021-09-25 | به صورت نوت شماره 2 اضافه گردید. |  |  | Noted and Closed.
7 | Ref. item 5 above: A separate row titled Differential protection scheme (self balancing/conventional) shall be added and according to NISOC letter NO. 372899 date 1400/10/30, Conventional shall be selected. |  | BK-SUR-ENG-ELE-00-03126 | 2022-02-20 | اعمال گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 19-Feb-22 |  |  |  |  | Date: