## TBE for PG
نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني مربوط به موقعیت W008N
Contract No: 9184 – 073 - 053 |  |  | TBE For Presssure Gauge
|  |  | Project Code |  | Package | Company code |  | Scope | Disc Code |  | Doc. Code | Sequence No. | Rev. Code
|  |  | BK |  | W008N | PEDCO |  | 110 | IN |  | TB | 0002 | D00
REQ. NAME : |  | MR for Pressure Gauge |  | BIDDER:
REQ. NO. : |  | RR-00-PS-110-IN-MR-0030 |  | NAME: |  |  | آسیا ابزاردقیق |  |  |  | پارس جهد |  | ساعی سامانگر صنعت سبز (4S) |  | سنگان صنعت
REQ. REV. : |  | D03 |  | QUOTATION NO.: |  |  | 21813-TECHNICAL PROPOSAL |  |  |  | PJ-PR-09-00021 |  | 140011016 |  | 1400-P-8716
EQUIPMENT TYPE : |  | Pressure Gauge |  | QUOTATION DATE:
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED
[7 empty] | A |  |  |  | B |  | C |  | D
A | Scope of Work And Supply
1 | Tag Number |  |  | PG-1601 & PG-1602
2 | Scope of Work And Supply |  |  | Pressure Gauge |  |  | Confirmed |  |  |  | Confirmed |  | Confirmed |  | Confirmed
3 | Delivary Date |  |  | B.V. |  |  | 1~2 months |  |  |  | 12~14 Weeks after AFC Drawings & Down Payment |  | 120 days after down payment. |  | 90 working Days after advanced payment and approved technical documents
4 | Delivary Place |  |  | Ex.Work |  |  | EXW Asia Instruments co |  |  |  | EXW Pars Jahd co ARAK |  | DDP |  | EX.WORKS
5 | Bid Validity Period |  |  | B.V. |  |  | 2 Weeks |  |  |  | 2 Weeks |  | 30 Days. |  | 30 days
6 | GUARANTEE |  |  | Requisition eighteen (18) months from the date of the Installation and Commissioning or twenty-four (24) months after the date of delivery of materials (whichever comes earlier) |  |  | Confirmed |  |  |  | 24 Month after shipment 18 Month after Installation |  | 24 Month after shipment 18 Month after Installation |  | confirmed
7 | MANUFACTURER (VENDOR LIST) |  |  | AVL |  |  | Confirmed by vendor but it is not listed in MOP |  |  |  | confirmed |  | confirmed |  | Confirmed
8 | SPARE PARTS |  |  | 5% complete set |  |  | Confirmed |  |  |  | Confirmed |  | Not Confirmed |  | confirmed
B | Technical Requirements
1 | Environmental / Process Condition |  |  | According to data sheet |  |  | Confirmed |  |  |  | Gauges accuracies will be effected by this tempreture and they should be protected by sunshade |  | Gauges accuracies will be effected by this tempreture and they should be protected by sunshade |  | confirmed
2 | Pressure Element Type |  |  | Bourdon |  |  | Confirmed |  |  |  | Confirmed |  | confirmed | confirmed | confirmed
3 | Pressure Element Material |  |  | Stainless Steel 316 |  |  | Confirmed |  |  |  | Confirmed |  | confirmed | confirmed | confirmed
4 | Calibration Range |  |  | As requested |  |  | Confirmed |  |  |  | Confirmed |  | confirmed | confirmed | confirmed
5 | Eng. Unit |  |  | Bar/Psi |  |  | Confirmed |  |  |  | Confirmed |  | confirmed | confirmed | confirmed
6 | Zero Adjustment |  |  | Yes |  |  | Confirmed |  |  |  | Confirmed |  | Confirmed | Confirmed | confirmed
7 | Mounting |  |  | As requested |  |  | Confirmed |  |  |  | mentioned in TO |  | Noted | confirmed | confirmed
8 | Ring Construction/Material |  |  | Screwed/ Stainless Steel |  |  | Confirmed |  |  |  | The Bayonet is available |  | Noted | confirmed | confirmed
9 | Dial Size |  |  | 150mm (Black graduation on white background) |  |  | Confirmed |  |  |  | Confirmed |  | Confirmed | Confirmed | confirmed
10 | Case Material |  |  | Stainless Steel 304 |  |  | Confirmed |  |  |  | Confirmed |  | Confirmed | Confirmed | confirmed
11 | Socket Material |  |  | Stainless Steel 316 |  |  | Confirmed |  |  |  | Confirmed |  | Confirmed | Confirmed | confirmed
12 | Connection Size |  |  | 1/2" NPTM |  |  | Confirmed |  |  |  | Confirmed |  | Confirmed | Confirmed | confirmed
13 | Movement Material |  |  | 316 S.S. |  |  | Confirmed |  |  |  | S.S. 304 |  | Confirmed |  | 304 S.S. mentioned in datasheet
14 | Accuracy |  |  | ±1% Full Scale |  |  | ±5% Full Scale |  |  | confirmed | confirmed |  | Confirmed |  | confirmed
15 | Over range Protection |  |  | 30% Full Scale |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed |  | confirmed
16 | Weather Protection |  |  | IP65 |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
17 | Blow-Out Protection |  |  | Back, Disc |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
18 | shatter proof & soild front |  |  | Yes |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
19 | Pressure valve protector |  |  | YES |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
20 | Oil Filled Case |  |  | Yes |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | confirmed | confirmed
21 | Manifold type for non-diaphragm seal items |  |  | 2 Valves |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
22 | Manifold Material |  |  | Stainless Steel 316 |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
23 | Manifold Connection (Instrument/Process) |  |  | 1/2"NPTF |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
24 | In Compliance with NACE Std. |  |  | As requested |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
25 | Manifold Vent/Drain Size & Rating |  |  | 1/4" NPTF & 3000 psi |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
26 | SS Name Plate |  |  | As requested |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
27 | Painting |  |  | Vendor 's Standard |  |  | Confirmed |  |  | Confirmed | confirmed |  | Confirmed | Confirmed | confirmed
C | Test and Inspection
1 | Test and Inspection
D | Document Requirements
1 | Country Of Origin |  |  | Contract |  |  | Germany |  |  |  | Pars Jahd Pressure Gauges & Manifold/ Iran Vee Lok Pressure limit valve/ Taiwan Pars Jahd or Vee Lok Syphon Tube/ Iran or Taiwan |  | IRAN |  | IRAN
2 | Material Test / Calibration Certificate |  |  | Requisition |  |  | Confirmed |  |  |  | Confirmed |  | To be submmited during manufacturing process |  | Confirmed
E | Level of Similar Experience in past 10 years |  |  | Vendor 's Quotation |  |  | Jetti, BBII,SARVAK AZAR |  |  |  | Reference list submitted. |  | more than 20 projects |  | refrence list is attached
F | Deviations / Alternatives
1 | Deviations (if any) |  |  | signed and stamped |  |  | Submitted |  |  |  | Submitted |  | Submitted |  | Submitted
G | Manufacturer's Location |  |  | - |  |  | Germany |  |  |  | ITALY |  | - |  | Tehran - Qom highway
H | PROPOSAL DOCUMENTATION
1 | Quality plan / ITP |  |  | shall be submitted |  |  | Submitted |  |  |  | Submitted |  | Submitted |  | Submitted
2 | Standard certificates |  |  | shall be submitted |  |  | Submitted |  |  | after PO | after PO |  | after PO |  | Submitted
3 | Confirmed scope of work & scope of supply as per MR |  |  | shall be submitted |  |  | Submitted |  |  | Submitted | Submitted |  | Submitted |  | Submitted
4 | Filled TBE |  |  | shall be submitted |  |  | Submitted |  |  | Submitted | Submitted |  | Submitted |  | Submitted
5 | Summary sheets |  |  | shall be submitted |  |  | Submitted |  |  | Submitted | Submitted |  | Submitted | Submitted | Submitted
7 | Reference list |  |  | shall be submitted |  |  | Submitted |  |  | Submitted | Submitted |  | Submitted | Submitted | Submitted
8 | Catalouges |  |  | shall be submitted |  |  | Submitted |  |  | Submitted | Submitted |  | Submitted | Submitted | Submitted
9 | Datasheet/ Drawing |  |  | shall be submitted |  |  | Submitted |  |  | After PO | After PO |  | Before Manufacturing | Submitted | Submitted
10 | Order code (Part No.) |  |  | shall be submitted |  |  | Submitted |  |  | Submitted | Submitted |  | Before Manufacturing | Submitted | Submitted
General Technical acceptance of Quotation: | [6 empty] | CA |  |  |  | A |  | A |  | A
Notes:
A : ACCEPTABLE (TECHNICALLY MEETS REQUIREMENT)
NA: NOT ACCEPTABLE (TECHNICALLY DOES NOT MEET REQUIREMENT)
CA: CONDITIONALLY ACCEPTED
INA: INFORMATION NOT AVAILABLE
N/A: NOT APPLICABLE