## TBE for TG
نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني مربوط به موقعیت W046S
Contract No: 9184 – 073 - 053 |  |  | TBE For Temperature Gauge
|  |  | Project Code |  | Package | Company code |  | Scope | Disc Code |  |  | Doc. Code |  | Sequence No. | Rev. Code
|  |  | BK |  | W046S | PEDCO |  | 110 | IN |  |  | TB |  | 0002 | D00
REQ. NAME : |  | MR for Temperature Gauge |  | BIDDER:
REQ. NO. : |  | RR-00-PS-110-IN-MR-0030 |  | NAME: |  |  | آسیا ابزاردقیق |  |  |  |  | پارس جهد |  |  | ساعی سامانگر صنعت سبز (4S) |  | سنگان صنعت
REQ. REV. : |  | D03 |  | QUOTATION NO.: |  |  | 21813-TECHNICAL PROPOSAL |  |  |  |  | PJ-PR-09-00021 |  |  | 140011016 |  | 1400-P-8716
EQUIPMENT TYPE : |  | Pressure Gauge |  | QUOTATION DATE:
NO. | DESCRIPTION |  |  | REFERENCE / SPECIFIED
[7 empty] | A |  |  |  |  | B |  |  | D |  | D
A | Scope of Work And Supply
1 | Tag Number |  |  | TG/TW-1301
2 | Scope of Work And Supply |  |  | Temperature Gauge |  |  | Confirmed |  |  |  |  | Confirmed |  |  | Confirmed |  | Confirmed
3 | Delivary Date |  |  | B.V. |  |  | 1~2 months |  |  |  |  | 20-22 weeks after AFC Docs and receiving down payment. |  |  | Confirmed |  | 90 working Days after advanced payment and approved technical documents
4 | Delivary Place |  |  | Ex.Work |  |  | EXW Asia Instruments co |  |  |  |  | EXW Pars Jahd Factory Arak-Iran 60% cash in advance as down payment and 40% before Shipping. | EXW Pars Jahd Factory Arak-Iran 60% cash in advance as down payment and 40% before Shipping. |  | Confirmed |  | EX.WORKS
5 | Bid Validity Period |  |  | B.V. |  |  | 2 Weeks |  |  |  |  | 2 Weeks | 2 Weeks |  | Confirmed |  | 30 days
6 | GUARANTEE |  |  | Requisition eighteen (18) months from the date of the Installation and Commissioning or twenty-four (24) months after the date of delivery of materials (whichever comes earlier) |  |  | Confirmed |  |  |  |  | 18 months after shipment or 12 months after installation. | 18 months after shipment or 12 months after installation. |  | Confirmed |  | confirmed
7 | MANUFACTURER (VENDOR LIST) |  |  | AVL |  |  | Confirmed by vendor but it is not listed in MOP |  |  |  |  | Please note that the Temperature Gauges manufacturer is Nuovafima Co., Italy and the Thermowells is Pars Jahd Co., Arak. | Please note that the Temperature Gauges manufacturer is Nuovafima Co., Italy and the Thermowells is Pars Jahd Co., Arak. |  | Confirmed |  | SANGAN SANAT
8 | SPARE PARTS |  |  | 5% complete set |  |  | Confirmed |  |  |  |  | Confirmed | Confirmed |  | Not Confirmed |  | Confirmed
B | Technical Requirements
1 | Environmental / Process Condition |  |  | According to data sheet |  |  | Confirmed |  |  |  |  | Not Confirmed |  |  | Confirmed |  | Confirmed
2 | Thermometer Type |  |  | Bimetal / Filled type (As requested) |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
3 | Calibrated Range |  |  | As requested |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
4 | Dial Size |  |  | 150 mm |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
5 | Dial Color |  |  | White with black Letter |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
6 | Case Material |  |  | Stainless Steel 304 |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
7 | Process Connection Size/ rating |  |  | 1 1/2 RTJ,/ API 3000 |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
8 | Eng. Unit |  |  | °C/ °F |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
9 | Accuracy |  |  | Better than ± 1% of full span |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
10 | Pointer Color / Material |  |  | Black / Metallic |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
11 | Stem Type / Material |  |  | Threaded / 316 SS |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
12 | Stem Diameter |  |  | 6 mm |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
13 | Ingress Protection |  |  | IP65 |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
14 | Window Material |  |  | Shatterproof Glass |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
15 | Zero Adjustment |  |  | Pointer |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
16 | Over range Protection |  |  | 1.5 times the maximum scale. |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
17 | Connection |  |  | Every Angle |  |  | Confirmed |  |  | Noted. | Noted. | Confirmed |  |  | Confirmed | Confirmed (Back ) | NOT Confirmed (Back )
18 | External Calibration Adjustment |  |  | Required |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
19 | Head Type |  |  | Oriantable Head |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
20 | Bulb Material |  |  | SS 316 |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
21 | Thermowell |  |  | Tapered Drilled Bar Stock |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
22 | Well conn. & Flange Material |  |  | As requested & Stainless Steel 316 |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
23 | Thermowell Connection |  |  | As requested |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
24 | In Complaince with Nace Standard |  |  | As requested |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
25 | Insertion Length (U) mm |  |  | As requested |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
26 | SS Name Plate |  |  | As requested |  |  | Confirmed |  |  | Confirmed |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
27 | Accessories for installation for remote type |  |  | As requested |  |  | Confirmed |  |  |  |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
C | Test and Inspection
1 | Test and Inspection |  |  | Project IDS, Requisition |  |  | Confirmed |  |  |  |  | Any applicable and available Test and Inspection would be issued after PO as per ITP. Please fine the attached simple ITP. |  |  | not specified |  | confirmed
D | Document Requirements
1 | Country Of Origin |  |  | Contract |  |  | Germany |  |  |  |  | Nuovafima Co., Italy. |  |  | not specified |  | made in iran
2 | Wake Frequency Calculaton |  |  | Requisition |  |  | After P.O. |  |  |  |  | After P.O. |  |  | not specified | NO Needed Velocity is 0 | NO Needed Velocity is 0
3 | Material Test / Calibration Certificate |  |  | Requisition |  |  | Confirmed |  |  |  |  | Confirmed |  |  | Confirmed | Confirmed | Confirmed
E | Level of Similar Experience in past 10 years |  |  | Vendor 's Quotation |  |  | Jetti, BBII,SARVAK AZAR |  |  |  |  | Refrence list submitted |  |  | not specified |  | refrence list submitted
F | Deviations / Alternatives
1 | Deviations (if any) |  |  | signed and stamped |  |  | Confirmed |  |  |  |  | Not Specified |  |  | not specified |  | is attached.
G | Manufacturer's Location |  |  | - |  |  | Not Specified |  |  |  |  | Not Specified |  |  | not specified |  | Tehran - Qom highway
H | PROPOSAL DOCUMENTATION
1 | Quality plan / ITP |  |  | shall be submitted |  |  | Submitted |  |  |  |  | Submitted |  |  | not specified |  | Submitted
2 | Standard certificates |  |  | shall be submitted |  |  | Submitted |  |  | Submitted |  | Submitted |  |  | not specified |  | Submitted
3 | Filled TBE |  |  | shall be submitted |  |  | Submitted |  |  | Submitted |  | Submitted |  |  | not specified | Submitted | Submitted
4 | Summary sheets |  |  | shall be submitted |  |  | Submitted |  |  | Submitted |  | Submitted |  |  | not specified | Submitted | Submitted
5 | Subvendor list (if any) |  |  | shall be submitted |  |  | Submitted |  |  | Submitted |  | Submitted |  |  | not specified | Submitted | Submitted
6 | Reference list |  |  | shall be submitted |  |  | Submitted |  |  | Submitted |  | Submitted |  |  | not specified | Submitted | Submitted
7 | Catalouges |  |  | shall be submitted |  |  | Submitted |  |  | Submitted |  | Submitted |  |  | not specified | Submitted | Submitted
8 | Datasheet/ Drawing |  |  | shall be submitted |  |  | Submitted |  |  | Submitted |  | Submitted |  |  | not specified | Submitted | Submitted
9 | Letter of Conformity |  |  | shall be submitted |  |  | Not Submitted |  |  | Not Submitted |  | Not Submitted |  |  | not specified | Not Submitted | Not Submitted
10 | Order code (Part No.) |  |  | shall be submitted |  |  | Submitted |  |  | Submitted |  | Submitted |  |  | not specified | Submitted | Submitted
General Technical acceptance of Quotation: | [6 empty] | CA |  |  |  |  | A |  |  | A |  | A
Notes:
A : ACCEPTABLE (TECHNICALLY MEETS REQUIREMENT)
NA: NOT ACCEPTABLE (TECHNICALLY DOES NOT MEET REQUIREMENT)
CA: CONDITIONALLY ACCEPTED
INA: INFORMATION NOT AVAILABLE
N/A: NOT APPLICABLE