## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR ON/OFF & SHUTDOWN VALVES
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | IN | DT | 0006 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR ON/OFF & SHUTDOWN VALVES نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | MAY.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: 'F9Z-708585
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR ON/OFF & SHUTDOWN VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | IN | DT | 0006 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | [7 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR ON/OFF & SHUTDOWN VALVES
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  | BK | PPL | PEDCO | 320 | IN | DT | 0006 | D00
REFERENCE DOCUMENTS :
| 1. Instrument & Control System Design Criteria |  |  |  |  | BK-PPL-PEDCO-320-IN-DC-0001_D00
| 2. P&ID - Gas Pipeline (to Siahmakan G.I. Station) |  |  |  |  | BK-PPL-PEDCO-320-PR-PI-0001_D02
| 3. P&ID - Condensate Pipeline (to Binak PU) |  |  |  |  | BK-PPL-PEDCO-320-PR-PI-0002_D02
| 4. Piping Material Specification |  |  |  |  | BK-PPL-PEDCO-320-PI-SP-0001_D01
| 5. Specification for Instrumentation |  |  |  |  | BK-GNRAL-PEDCO-000-IN-SP-0001_D03
| 6. Specification For On-off Shut Down Valves(ESDVMOV) |  |  |  |  | BK-GNRAL-PEDCO-000-IN-SP-0006_D00
| 7. Instrument Hook-Up Diagram |  |  |  |  | BK-PPL-PEDCO-320-IN-DG-0002_D00
| 8. Process Basic of Design |  |  |  |  | BK-GNRAL-PEDCO-000-PR-DB-0001_D01

## Note
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR ON/OFF & SHUTDOWN VALVES
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  | BK | PPL | PEDCO | 320 | IN | DT | 0006 | D00
GENERAL NOTES:
1. Calculations shall be provided for each completely piped actuated valve assembly (including solenoid valve), the stroking times i.e. to close and to open.
2. The duty, failure action and stroke time shall all be approved by the Purchaser.
3. The actuator shall be designed to operate the valve through its full stroke.
4. The full stroke time for on-off valve which is less or equal than 4" size, shall be max. 5 second and for valves greater than 4", 1 second shall be added to the 4 sec for each increment of 1" in valve size. The maximum fully stroke time shall be 10 seconds.
5. The piping indicates corrosion allowance selected as per document "Piping & Pipeline Material Specification, No. " BK-PPL-PEDCO-320-PI-SP-0001 "
6. Hydro-test duration shall be in accordance with API 6D.
7. All ball valves shall be fitted with suitable 'end of travel' stops at the fully open and fully closed positions and a local position indicator. The design shall prevent the ingress of foreign material and corrosion products which would impair the operation of the stops. Devices capable of locking the valves in their safe position (ESDV in open or closed position) shall be provided for maintenance and shall be vendor's standard proven design.
8. Vendor shall guarantee and demonstrate the required stroking speed, during the Functional Test (FAT).
9. All accessories shall be mounted, together with solenoid valve, etc., on a 316SS sub-plate. Tubing shall be suitably sized TP 316L stainless steel with stainless steel double ferrule compression fittings.
10. Solenoid valve shall be selected in accordance with low power type.
11. All on/off valves shall be preferably fitted with single acting, spring return pnumatic actuators, completed with mounting kit. Also Partial Stroking test or pilot valve to be considered.
12. The actuator shall be fail-safe in operation (as specified in data sheets) in loss of electrical signal or loss of air supply.
13. The spring return actuator shall be "pre stressed".
14. Pneumatic actuators will be sized on the basis of a minimum safety factor of 1.5 and a minimum air pressure of 3 Barg. The valve actuator torque shall be in excess of the required valve torque under all operating conditions.
15. All actuators and accessories shall be clearly and permanently identified by nameplate. The nameplate shall be in stainless steel and affixed to the VALVE, actuator and accessories.
16.For application in sour gas services, as indicated in individual data sheets, material of body, trim and all other wetted metal parts in contact with the sour gas shall meet the requirements of NACE, MR-01-75, latest edition.
17. Material Test Certificate and calibration Certificate for all transmitters to be submitted by Vendor.
18. Manual Reset to be consider for all Emergency Shut off solenoids as per P&ID.
19.Disc/seat material shall be resilient to give a tight shut off feature.
20 .According to "Process Basic of Design" Document, Environmental Condition For Field Instrumentation of BINAK Complex Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C)
Minimum ambient temperature: 5 (°C)
Maximum steel surface exposed to sun: 85 (°C)
Maximum summer dry bulb: 50 (°C)
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0

## ESDV-3201
نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR ON/OFF & SHUTDOWN VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 6
9038 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | IN | DT | 0006 | D00
On-Off Valve
TAG NO: |  | ESDV-3201 | P&ID NO : |  | BK-PPL-PEDCO-320-PR-PI-0001_D01 ( page 1 of 3) | [6 empty] | SERVICE: |  | FROM DEHYDRATION (PK-2101)
FLUID STATE: | GAS |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone 2, IIB T4
SERVICE CONDITION | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [7 empty] | kg/h |  | - | 17170.8 | - | -
| 2 | INLET PRESSURE | [7 empty] | bar(g) |  | 50.92 |  | - | -
| 3 | OUTLET PRESSURE | [7 empty] | bar(g) |  | 50.92 |  | - | -
| 4 | DIFFERENTIAL PRESSURE | [7 empty] | bar |  | - |  | - | 63
| 5 | INLET TEMPERATURE | [7 empty] | °C |  | 58.27 |  | - | -
| 6 | DENSITY(Mix./Gas/Liquid) | [7 empty] | kg/m3 |  | 22.86 |  | - | -
| 7 | VISCOSITY (GAS/LIQ.) | [7 empty] | CP |  | 0.013 |  | - | -
| 8 | VAPOR PRESSURE Pv | [7 empty] | bar(a) |  | - |  | - | -
| 9 | CRITICAL PRESSURE | [7 empty] | bar(g) |  | 104.9 |  | - | -
LINE | 10 | PIPE LINE SIZE | IN |  | 6" |  |  |  |  | ACTUATOR | 52 | TYPE |  | Single Acting , Spring Return
|  | & SCHEDULE | OUT |  | 6" | [5 empty] | 53 | SIZE |  | VTA | VTA
| 11 | PIPNG CLASS/PIPE LINE INSULATION |  |  | FN05 / PAINTED | [5 empty] | 54 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 55 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  | 6" | [5 empty] | 56 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP |  |  | As per Specification For Pipeline Material (Note 5) | [5 empty] | 57 | AVAILABLE AIR SUPPLY PRESS. |  | MAX/NOR/MIN: 8/7/4.5 barg (Note 14)
| 15 | MFR. & MODEL |  |  | VTA | [5 empty] | 58 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  | A216 Gr. WCB (Note 5) | [5 empty] | 59 | TRAVELING TIME |  | 6 Sec.
| 17 | LINER MATERIAL / ID |  |  | VTA | [5 empty] | 60 | FUNCTION |  | On/Off
| 18 | END | ANSI Class |  | 6" |  | 600# |  |  |  | 61 | LOCAL POSITION INDICATOR |  | Required
|  | CONNECTION |  |  | 6" | [5 empty] | 62 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  | RTJ | [5 empty] | 63 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  | N/A | [5 empty] | 64 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  | N/A | [5 empty] | 65 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  | Standard | [5 empty] | 66 | MFR. & MODEL |  | VTA
| 23 | LUBE & ISO VALVE |  |  | No |  |  |  |  | POSITIONER | 67 | TYPE |  | N/A
| 24 | PACKING MATERIAL | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 68 | MFR. & MODEL |  | N/A
| 25 | ENTRY DESIGN |  |  | Top Entry | [5 empty] | 69 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  | Yes | [5 empty] | 70 | GAUGES |  | N/A
TRIM | 27 | TRIM TYPE |  |  | VTA | [5 empty] | 71 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  | VTA |  |  | VTA |  |  | 72 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 75 | TAG NO. : |  | EZSC-3201 /EZSO-3201
| 30 | BALANCED / UNBALANCED |  |  | VTA | [5 empty] | 76 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT | VTA |  | VTA | VTA |  |  | 77 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL MATERIAL |  |  | SS316+RPTFE (Note 5) | [5 empty] | 78 | ACTUATION POINT |  | Fully Open/Close
| 33 | DISK/ SEAT MATERIAL | SEAT TYPE |  | VTA (Note 19) |  | Soft seat (VTC) |  |  |  | 79 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  | VTA | [5 empty] | 80 | WEATHER PROTECTION |  | IP-65
| 35 | STEM MATERIAL |  |  | forged, 13% chromium steel (As per reference 6) | [5 empty] | 81 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d", IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  | ANSI Class VI | [5 empty] | 82 | MFR. & MODEL |  | VTA
| 37 | [8 empty] | AIR SET | 83 | SET PRESSURE |  | VTA
SOLENOID VALVE | 38 | TAG NO |  |  | ESOV-3201, PSOV-3201 | [5 empty] | 84 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  | 3 Way | [5 empty] | 85 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 86 | MFR. & MODEL |  | VTA
| 41 | ELE. CERTIFICATE | ELE. CONNECTION |  | EEx "d", IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 87 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  | Yes (Note 18) | [5 empty] | 88 | HYDRO PRESSURE |  | Required
| 43 | POWER SUPPLY |  |  | 24 VDC | [5 empty] | 89 | FUNCTIONAL TEST |  | Required
| 44 | PNEU. CONNECTION |  |  | 1/4" NPT , VTA | [5 empty] | 90
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  | No | [5 empty] | 91
| 46 | BLOCK RELAY |  |  | No | [5 empty] | 92
| 47 | QUICK EXHUST |  |  | Yes |  |  |  |  | OPTION | 93 | PASSIVE FIRE PROTECTION |  | No
| 48 | FILTER REGULATOR |  |  | Yes | [5 empty] | 94 | API 6FA REQUIREMENTS |  | Yes
| 49 | VOLUME TANK |  |  | Yes | [5 empty] | 95 | SIL 3 REQUIREMENTS |  | Yes
| 50 | MECHANICAL POSITION INDICATOR |  |  | Required | [5 empty] | 96 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MANUAL PNE. BYPASS VALVE FOR SOLENOID VALVE |  |  | Yes
NOTE: | VTA : VENDOR TO ADVISE
** PMS: Piping Material Specification

## ESDV-3202
نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR ON/OFF & SHUTDOWN VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 6
9038 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | IN | DT | 0006 | D00
On-Off Valve
TAG NO: |  | ESDV-3202 | P&ID NO : |  | BK-PPL-PEDCO-320-PR-PI-0001_D01 ( page 3 of 3) | [6 empty] | SERVICE: |  | FROM PIG LAUNCHER (PL-3201)
FLUID STATE: | GAS |  | PHASE: |  | GAS | [6 empty] | AREA CLASSIFICATION: |  | Zone 2, IIB T4
SERVICE CONDITION | [9 empty] | UNITS |  | Max Flow | Norm. Flow | Min. Flow | Shut-Off
| 1 | FLOW RATE | [7 empty] | kg/h |  | - |  | - | -
| 2 | INLET PRESSURE | [7 empty] | bar(g) |  | 40 |  | - | -
| 3 | OUTLET PRESSURE | [7 empty] | bar(g) |  | 40 |  | - | -
| 4 | DIFFERENTIAL PRESSURE | [7 empty] | bar |  | - |  | - | 63
| 5 | INLET TEMPERATURE | [7 empty] | °C |  | 31.3 |  | - | -
| 6 | DENSITY(Mix./Gas/Liquid) | [7 empty] | kg/m3 |  | 49.09 |  | - | -
| 7 | VISCOSITY (GAS/LIQ.) | [7 empty] | CP |  | 0.012 |  | - | -
| 8 | VAPOR PRESSURE Pv | [7 empty] | bar(a) |  | - |  | - | -
| 9 | CRITICAL PRESSURE | [7 empty] | bar(g) |  | 104.9 |  | - | -
LINE | 10 | PIPE LINE SIZE | IN |  | 8" |  |  |  |  | ACTUATOR | 52 | TYPE |  | Single Acting , Spring Return
|  | & SCHEDULE | OUT |  | 8" | [5 empty] | 53 | SIZE |  | VTA | VTA
| 11 | PIPNG CLASS/PIPE LINE INSULATION |  |  | FN05 / PAINTED | [5 empty] | 54 | SPRING FAIL ACTION |  | Fail to Close
VALVE BODY & BONNET | 12 | TYPE |  |  | Full Bore Ball Valve/Trunnion Mounted | [5 empty] | 55 | MAX ALLOWABLE PRESSURE |  | VTA
| 13 | SIZE |  |  | 8" | [5 empty] | 56 | MIN REQUIRES PRESSURE |  | VTA
| 14 | MAX PRESS./TEMP |  |  | As per Specification For Pipeline Material (Note 5) | [5 empty] | 57 | AVAILABLE AIR SUPPLY PRESS. |  | MAX/NOR/MIN: 8/7/4.5 barg (Note 14)
| 15 | MFR. & MODEL |  |  | VTA | [5 empty] | 58 | BENCH RANGE |  | VTA
| 16 | BODY / BONNET MATL |  |  | A216 Gr. WCB (Note 5) | [5 empty] | 59 | TRAVELING TIME |  | 8 Sec.
| 17 | LINER MATERIAL / ID |  |  | VTA | [5 empty] | 60 | FUNCTION |  | On/Off
| 18 | END | ANSI Class |  | 8" |  | 600# |  |  |  | 61 | LOCAL POSITION INDICATOR |  | Required
|  | CONNECTION |  |  | 8" | [5 empty] | 62 | ACT. ORIENTATION |  | VTA
| 19 | FLG FACE FINISH |  |  | RTJ | [5 empty] | 63 | HAND WHEEL TYPE |  | Declutchable side mounted
| 20 | END EXT./MATL. |  |  | N/A | [5 empty] | 64 | ADJUSTABLE LIMIT STOP |  | Yes
| 21 | FLOW DIRECTION |  |  | N/A | [5 empty] | 65 | INPUT SIGNAL |  | 24VDC
| 22 | TYPE OF BONNET |  |  | Standard | [5 empty] | 66 | MFR. & MODEL |  | VTA
| 23 | LUBE & ISO VALVE |  |  | No |  |  |  |  | POSITIONER | 67 | TYPE |  | N/A
| 24 | PACKING MATERIAL | PACKING TYPE |  | PTFE |  |  | Standard |  |  | 68 | MFR. & MODEL |  | N/A
| 25 | ENTRY DESIGN |  |  | Top Entry | [5 empty] | 69 | ON INCR SIGNAL OUTPUT INCR / DECR |  | N/A
| 26 | NACE REQUIREMENTNACE (MR-0175/ISO 15156) |  |  | Yes | [5 empty] | 70 | GAUGES |  | N/A
TRIM | 27 | TRIM TYPE |  |  | VTA | [5 empty] | 71 | CAM CHARACTERISTIC |  | N/A
| 28 | SIZE | RATED TRAVEL |  | VTA |  |  | VTA |  |  | 72 | AIR CONNECTION |  | N/A
| 29 | CHARACTERISTICS |  |  | On/Off |  |  |  |  | LIMIT SWITCHES | 75 | TAG NO. : |  | EZSC-3202 /EZSO-3202
| 30 | BALANCED / UNBALANCED |  |  | VTA | [5 empty] | 76 | TYPE | QUANTITY | Magnetically operated ‘REED’ contacts | 2
| 31 | RATED Cv | FL | XT | VTA |  | VTA | VTA |  |  | 77 | CONTACTS / RATING |  | 110V DC , 10A
| 32 | PLUG / BALL MATERIAL |  |  | SS316+RPTFE (Note 5) | [5 empty] | 78 | ACTUATION POINT |  | Fully Open/Close
| 33 | DISK/ SEAT MATERIAL | SEAT TYPE |  | VTA (Note 19) |  | Soft seat (VTC) |  |  |  | 79 | ENCLOSURE MATERIAL |  | Die Cast Aluminum
| 34 | CAGE / GUIDE MATERIAL |  |  | VTA | [5 empty] | 80 | WEATHER PROTECTION |  | IP-65
| 35 | STEM MATERIAL |  |  | forged, 13% chromium steel (As per reference 6) | [5 empty] | 81 | ELEC. CERTIFICATE | ELEC. CONNECTION | EEx "d", IIB T4 | ISO M20 × 1.5
| 36 | LEAKAGE CLASS |  |  | ANSI Class VI | [5 empty] | 82 | MFR. & MODEL |  | VTA
| 37 | [8 empty] | AIR SET | 83 | SET PRESSURE |  | VTA
SOLENOID VALVE | 38 | TAG NO |  |  | ESOV-3202, PSOV-3202 | [5 empty] | 84 | PNEUMATIC CONNECTION |  | 1/4" NPT
| 39 | TYPE |  |  | 3 Way | [5 empty] | 85 | GAUGES | FILTER | Required | Required
| 40 | BODY MATERIAL | WEATHER IP. |  | AISI 316 S.S |  |  | IP-65 |  |  | 86 | MFR. & MODEL |  | VTA
| 41 | ELE. CERTIFICATE | ELE. CONNECTION |  | EEx "d", IIB T4 |  |  | ISO M20 x 1.5 |  | TEST | 87 | ANSI/FCI LEAKAGE CLASS |  | Required
| 42 | MANUAL RESET |  |  | Yes (Note 18) | [5 empty] | 88 | HYDRO PRESSURE |  | Required
| 43 | POWER SUPPLY |  |  | 24 VDC | [5 empty] | 89 | FUNCTIONAL TEST |  | Required
| 44 | PNEU. CONNECTION |  |  | 1/4" NPT , VTA | [5 empty] | 90
SPECIAL / ACCESS. | 45 | FUSIBLE LEAKAGE |  |  | No | [5 empty] | 91
| 46 | BLOCK RELAY |  |  | No | [5 empty] | 92
| 47 | QUICK EXHUST |  |  | Yes |  |  |  |  | OPTION | 93 | PASSIVE FIRE PROTECTION |  | No
| 48 | FILTER REGULATOR |  |  | Yes | [5 empty] | 94 | API 6FA REQUIREMENTS |  | Yes
| 49 | VOLUME TANK |  |  | Yes | [5 empty] | 95 | SIL 3 REQUIREMENTS |  | Yes
| 50 | MECHANICAL POSITION INDICATOR |  |  | Required | [5 empty] | 96 | PARTIAL STROKING VALVE TEST |  | Yes
| 51 | MANUAL PNE. BYPASS VALVE FOR SOLENOID VALVE |  |  | Yes
NOTE: | VTA : VENDOR TO ADVISE
** PMS: Piping Material Specification