## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از6
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | IN | DT | 0005 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | MAY. 2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | MAR. 2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  | F9Z-708584
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | IN | DT | 0005 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | IN |  | DT | 5 | D01
REFERENCE DOCUMENTS :
|  | Instrument & Control System Design Criteria | [5 empty] | BK-PPL-PEDCO-320-IN-DC-0001_D00
|  | P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D02
|  | P&ID - Condensate Pipeline (to Binak PU) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0002_D02
|  | Piping Material Specification | [5 empty] | BK-GCS-PEDCO-120-PI-SP-0001_D01
|  | Specification For Instrumentation | [5 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001_D03
|  | Specification For Pressure Safety Valves(PSV) | [5 empty] | BK-GNRAL-PEDCO-000-IN-SP-0007_D00
|  | Instrument Hook-Up Diagram | [5 empty] | BK-PPL-PEDCO-320-IN-DG-0002_D00
D01

## Note 1
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  | BK | PPL | PEDCO | 320 | IN | DT | 0005 | D01
GENERAL NOTES:
1- The pressure relief valves and its accessories shall be supplied pre-assembled. Valves shall be supplied as a whole, complete with all the accessories like cap, lifting lever, test gag, etc. All threaded and flanged openings shall be suitably covered to prevent entry of foreign material.
2- Effective discharge coefficient of pressure relief valves shall be 0.975 for gas and vapor and 0.62 for liquid services as a maximum.
3- The valve size shall be based on size calculations for the worst of all cases that might cause the valve to blow. For flanged pressure relief valves the orifice letter designation and the corresponding relieving area indicated in the EPC Contractor's data sheet will be as per API-526.
4- For a valve of given inlet and outlet sizes and letter designation, relieving area of the valves offered by Vendor, shall meet those in API-526 as a minimum.
5- The set pressure, over pressure and relieving pressure of the PSV depending upon maximum allowable working pressure and accumulation as per API Standard 520 Part I, and ASME Section VIII Division I or ASME Section I as the case may be.
6- If the set pressure is less than maximum allowable working pressure (MAWP), the overpressure could be more than accumulation. However, if PSV set pressure is same as MAWP, the accumulation and overpressure cannot exceed the accumulation. The relieving pressure would be set pressure plus overpressure.
6- ASME SECTION VIII DIV 1 stated a 10 % allowable over pressure over set pressure to achieve full lift of a single relief valve for blocked case. If the set pressure as maximum allowable working pressure (MAWP) set, the accumulation and over pressure is same and it is 10% over MAWP.
7- Emission shall be less than 85 dBA at 1 m distance from the valve.
8- For flanged valves, inlet and outlet sizes and ratings and center to flange face dimensions shall be in accordance with API-526. Dimensional tolerances shall be as mentioned there. If the design of pressure relief valve is such that liquid can collect on the discharge side of the disk, the valve shall be equipped with a drain at the lowest point where liquid can collect.
9- Valves shall, in general, be of the direct spring loaded full nozzle with minimum inlet flange rating of 300#, unless otherwise specified.
10- Nozzles of the forged type are preferable.
11- All valves shall be provided with a cap over the adjusting bolt.
12- Valve spring design shall not permit an adjustment of more than 5% above or 5% below that for which the valve is marked; unless the setting is within the spring design range established by the manufacturer or is determined to be acceptable to the manufacturer. The allowable tolerances in set pressures are as below: - ±0.14 bar for set pressures up to and including 4.8 barg. - ±3% for set pressures above 4.8 barg.
13- Materials of construction shall be suitable for the environmental conditions and the process conditions identified in the relevant instrument datasheets. Provision of corrosion resistant materials shall be considered for conventional valves for corrosive fluid. Materials to be used shall be in accordance with project piping material specification and relevant datasheets
14. In general, unless specifically identified otherwise in this specification and attachments, process wetted materials which are in contact with Corrosive Services (H2S, CO2, H2O), shall comply with the requirements of .. NACE MR0175/ISO 15156 . Body material shall normally be carbon steel and generally adhered to and consistent with project document “Piping Material Specification”.
15. According to "Specification For Pressure Safety Valves(PSV)", Valve bonnet or spring housing material shall be the same as the valve body material
16-According to "Process Basic of Design" Document, Environmental Condition For Field Instrumentation of BINAK Complex Shall Be Considered As Per The Following:
Maximum ambient temperature: 50 (°C)
Minimum ambient temperature: 5 (°C)
Maximum steel surface exposed to sun: 85 (°C)
Maximum summer dry bulb: 50 (°C)
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
D01

## PSV-3201
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  | BK | PPL |  | PEDCO | 320 | IN | DT |  | 0005 | D01
Item |  | Data Category | Technical Features | [7 empty] | Project Data & Requirements
1 |  | GENERAL | Tag Number | [7 empty] | PSV-3201
2 |  |  | P&ID NO and Page : | [7 empty] | BK-PPL-PEDCO-320- PR-PI-0001 (1 of 3)
3 |  |  | Service | [7 empty] | Pig Launcher
4 |  |  | Inlet Line No. |  |  | Outlet Line No. |  |  |  |  | FL-113-0002-AN07-1"-PT |  |  |  | GAS-113-0003-FN05-1"-PT
5 |  |  | Discharge to | [7 empty] | To LP Flare Header
6 |  |  | Protect Equipment | [7 empty] | Launcher
7 |  |  | Area Clacification for Discharge | [7 empty] | Zone 2, IIB T4
8 |  |  | Sour Service | [7 empty] | Yes
9 |  |  | NACE MR0175/ISO 15156 Compliance | [7 empty] | Yes
10 |  | BASIS | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
11 |  |  | Design Type |  |  | Safety, Relief, Safety-Relief |  |  |  |  | Saftey
12 | [5 empty] | Conventional, Bellow, Pilot Op. |  |  |  |  | Conventional
13 |  |  | Bonnet Type | [7 empty] | Closed
14 |  | PROCESS CONDITIONS (note 2) | Fluid / Phase / State | [7 empty] | Gas / 1-phase / Vapor
15 |  |  | Ambient Temperature °C | [7 empty] | 5-50 |  |  |  | 85
16 |  |  | Temperature °C |  |  | Operating |  |  |  |  | 58.3
17 |  |  | Pressure Barg |  |  | Operating |  |  |  |  | 50.9
18 |  |  | Oper. Temperature °C |  |  | RelievingTemp. °C |  |  |  |  | 58.30 |  |  |  | 103.9
19 |  |  | Required Capacity kg/h | [7 empty] | 1799.993
20 |  |  | Molecular Mass |  |  | Sp. Gr.@ relief Tmp kg/m3 |  |  |  |  | 24.58 |  |  |  | 1.94
21 |  |  | Oper. Pressure barg |  |  | Set Pressure barg |  |  |  |  | 50.90 |  |  |  | 62
22 |  |  | Back Pressure Barg |  |  | Constant |  |  |  |  | 0.5
23 | [5 empty] | Variable |  |  |  |  | 0
24 | [5 empty] | Total |  |  |  |  | 0.5
25 |  |  | % Allowable Overpressure | [7 empty] | 21%
26 |  |  | Over Pressure Factor | [7 empty] | 1.21
27 |  |  | Compressibility Factor (Z) | [7 empty] | 0.839
28 |  |  | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 508.1
29 |  |  | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.448
30 |  |  | Density @ Oper. kg/m3 temprature & pressure | [7 empty] | 55.86
31 |  |  | Operating Viscosity cP | [7 empty] | 0.0137
32 |  |  | Barometric Pressure (psia) | [7 empty] | 14.37
33 |  | SELECTION | Design Code |  |  | Sizing Basis |  |  |  |  | API 520 |  |  |  | -
34 |  |  | pressure relieving and de-pressurising systems Code | [7 empty] | API 521
35 |  |  | Design of Construction | [7 empty] | API 521
36 |  |  | Scenarios | [7 empty] | fire
37 |  |  | Basis of Selection | [7 empty] | fire
38 |  |  | Calculated Area cm² | [7 empty] | 0.294
39 |  |  | Selected Area cm² | [7 empty] | 0.709
40 |  |  | Accumulation AC % | [7 empty] | 121
41 |  |  | Orifice Designation | [7 empty] | D
42 |  | CONNECTIONS | Size: Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
43 |  |  | Rating & Facing : Inlet |  |  | Outlet |  |  |  |  | #600 RF |  |  |  | #150 RF
44 |  | MATERIALS (VTC) | Body and Bonnet | [7 empty] | ASTM A105 (Note 14)
45 |  |  | Seat and Disc (Trim) | [7 empty] | SS 316+RPTFE (Note 14)
46 |  |  | Nozzle | [7 empty] | SS 316 (Note 14)
47 |  |  | Guide and Rings | [7 empty] | SS 316 (Note 14)
48 |  |  | Spring | [7 empty] | ASTM A105 (Note 15)
49 |  |  | Bellows | [7 empty] | N/A
50 |  | OPTIONS | Cap without Lever: Screwed or Bolted | [7 empty] | Screwed cap
51 |  |  | Lifting Lever: Plain or Packed | [7 empty] | N/A
52 |  |  | Test Gage | [7 empty] | Yes
53 |  |  | With Rupture Disc | [7 empty] | No
54 |  |  | Flame Arrestor | [7 empty] | No
55 |  |  | Hydro Test | [7 empty] | Required
56 |  |  | Seat Leakage Test | [7 empty] | Required
57 |  |  | Compliance Standard | [7 empty] | According to MR-0175 / ISO15156
58 |  | PURCHASE | Manufacturer | [7 empty] | will be finalized later
59 |  |  | Model | [7 empty] | will be finalized later
60 |  |  | Serial No. | [7 empty] | will be finalized later
Main Notes:
VTA : Vendor to Advise in bidding stage VTC : Vendor to confirm in bidding stage N/A: Not applicable
D01

## PSV-3202
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATASHEETS FOR PRESSURE & SAFETY RELIEF VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 6 از 6
9184 – 073 - 053 |  |  |  | BK | PPL |  | PEDCO | 320 | IN | DT |  | 0005 | D01
Item |  | Data Category | Technical Features | [7 empty] | Project Data & Requirements
1 |  | GENERAL | Tag Number | [7 empty] | PSV-3202
2 |  |  | P&ID NO and Page : | [7 empty] | BK-PPL-PEDCO-320- PR-PI-0001 (3 of 3)
3 |  |  | Service | [7 empty] | Pig Receiver
4 |  |  | Inlet Line No. |  |  | Outlet Line No. |  |  |  |  | GAS-113-0014-FN05-1"-PT |  |  |  | FL-113-0004-AN07-2"-PT
5 |  |  | Discharge to | [7 empty] | To Existing Flare System
6 |  |  | Protect Equipment | [7 empty] | Receiver
7 |  |  | Area Clacification for Discharge | [7 empty] | Zone 2, IIB T4
8 |  |  | Sour Service | [7 empty] | Yes
9 |  |  | NACE MR0175/ISO 15156 Compliance | [7 empty] | Yes
10 |  | BASIS | Nozzle (Full, Semi) | [7 empty] | Full Nozzle
11 |  |  | Design Type |  |  | Safety, Relief, Safety-Relief |  |  |  |  | Relief
12 | [5 empty] | Conventional, Bellow, Pilot Op. |  |  |  |  | Conventional
13 |  |  | Bonnet Type | [7 empty] | Closed
14 |  | PROCESS CONDITIONS (note 2) | Fluid / Phase / State | [7 empty] | Gas / 1-phase / Vapor
15 |  |  | Ambient Temperature °C | [7 empty] | 5-50 |  |  |  | 85
16 |  |  | Temperature °C |  |  | Operating |  |  |  |  | 31.3
17 |  |  | Pressure Barg |  |  | Operating |  |  |  |  | 40
18 |  |  | Oper. Temperature °C |  |  | RelievingTemp. °C |  |  |  |  | 31.30 |  |  |  | 48.51
19 |  |  | Required Capacity kg/h | [7 empty] | 1132.12
20 |  |  | Molecular Mass |  |  | Sp. Gr.@ relief Tmp kg/m3 |  |  |  |  | 24.58 |  |  |  | 2.58
21 |  |  | Oper. Pressure barg |  |  | Set Pressure barg |  |  |  |  | 40 |  |  |  | 62
22 |  |  | Back Pressure Barg |  |  | Constant |  |  |  |  | 0.5
23 | [5 empty] | Variable |  |  |  |  | 0
24 | [5 empty] | Total |  |  |  |  | 0.5
25 |  |  | % Allowable Overpressure | [7 empty] | 21%
26 |  |  | Over Pressure Factor | [7 empty] | 1.21
27 |  |  | Compressibility Factor (Z) | [7 empty] | 0.846
28 |  |  | Latent Heat of Vaporization (Kj/Kg) | [7 empty] | 557.5
29 |  |  | Ratio of Specific Heats(Cp/Cv) | [7 empty] | 1.448
30 |  |  | Density @ Oper. kg/m3 temprature & pressure | [7 empty] | 49.09
31 |  |  | Operating Viscosity cP | [7 empty] | -
32 |  |  | Barometric Pressure (psia) | [7 empty] | 14.37
33 |  | SELECTION | Design Code |  |  | Sizing Basis |  |  |  |  | API 520 |  |  |  | -
34 |  |  | pressure relieving and de-pressurising systems Code | [7 empty] | API 521
35 |  |  | Design of Construction | [7 empty] | API 521
36 |  |  | Scenarios | [7 empty] | fire
37 |  |  | Basis of Selection | [7 empty] | fire
38 |  |  | Calculated Area cm² | [7 empty] | 0.188
39 |  |  | Selected Area cm² | [7 empty] | 0.709
40 |  |  | Accumulation AC % | [7 empty] | 121
41 |  |  | Orifice Designation | [7 empty] | D
42 |  | CONNECTIONS | Size: Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
43 |  |  | Rating & Facing : Inlet |  |  | Outlet |  |  |  |  | #600 RF |  |  |  | #150 RF
44 |  | MATERIALS (VTC) | Body and Bonnet | [7 empty] | ASTM A105 (Note 14)
45 |  |  | Seat and Disc (Trim) | [7 empty] | SS 316+RPTFE (Note 14)
46 |  |  | Nozzle | [7 empty] | SS 316 (Note 14)
47 |  |  | Guide and Rings | [7 empty] | SS 316 (Note 14)
48 |  |  | Spring | [7 empty] | ASTM A105 (Note 15)
49 |  |  | Bellows | [7 empty] | N/A
50 |  | OPTIONS | Cap without Lever: Screwed or Bolted | [7 empty] | Screwed cap
51 |  |  | Lifting Lever: Plain or Packed | [7 empty] | N/A
52 |  |  | Test Gage | [7 empty] | Yes
53 |  |  | With Rupture Disc | [7 empty] | No
54 |  |  | Flame Arrestor | [7 empty] | No
55 |  |  | Hydro Test | [7 empty] | Required
56 |  |  | Seat Leakage Test | [7 empty] | Required
57 |  |  | Compliance Standard | [7 empty] | According to MR-0175 / ISO15156
58 |  | PURCHASE | Manufacturer | [7 empty] | will be finalized later
59 |  |  | Model | [7 empty] | will be finalized later
60 |  |  | Serial No. | [7 empty] | will be finalized later
Main Notes:
VTA : Vendor to Advise in bidding stage VTC : Vendor to confirm in bidding stage N/A: Not applicable
D01