## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GNRAL-PEDCO-000-IN-SP-0004 |  |  |  |  | EPC Contractor Tr. No.:BK-HD-PEDCO-T-0029 |  |  | Transmittal Date: 04 ـAug 2021
Document Title: Specification For Instrument and Control of Package Unit System (PU) |  |  |  |  | PEDCO Tr. No.:BK-HD-PEDCO-T-0029 |  |  | Transmittal Date: 04 ـAug 2021
[5 empty] | CRS No:PEDCO- CRS-BK-GNRAL-PEDCO-000-IN-SP-0004_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Control and instrumentation Design Creiteria shall be considered. |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | all document are compatible with each other
2 | Complementary Documents like P&IDs, Earting principle, FAT/SAT procedure shall be considered. |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | all document are compatible with each other
3 | Please concider following items in standard section: IPS-C-IN-210 IPS-G-IN-160 |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | There is no IPS standard with this code IPS-C-IN-210 and IPS-G-IN-210 has been reffered The other code added to document
4 | Below note shall be added end of standard section: "Vendor shall state the additional Codes and Standards if necessary." |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | Implemented
5 | applicable items related to the specification shall be mentioned in Abbreviation section . (for example BDV,UV and other cases shall be deleted) |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | Implemented
6 | its recommended to specify environment condition (for area and rack room) in addition of reffer to Process Basis of Design” Doc. No. “BK-GNRAL-PEDCO- 000-PR-BD-0001 |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | Due to prevent constrating to reissue all documents in case of any modification in environment data we suggest you to avoid data duplicating in documents if acclicable and accept referenced data.
7 | Priority of Documents shall be specified. |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | Order of precedence section added
8 | Failt Tolerant shall be mentioned |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | Mentioned on section 9.2.2 Reliability and availability
9 | Number of laptop and WS shall be mentioned |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | Implemented
10 | Serial link for interface between UCP and DCS shall be specified exactly. |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | Implemented
11 | Spare parts and special tools shall be checked according to Client procedure and contract. |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | has been refered in spare part section
12 | Type of Packages shall be specified and listed according to specification.(Type A,B,C) |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | This is a general specification and
13 | vendor is responsible for loose items .this item shall be mentioned in document. |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | Noted.
14 | UCP Panel (dimension, painting,IP and other iteems )shall be specified |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | has been refered to specification for painting BK-GNRAL-PEDCO-000-PI-SP-0006
15 | EEXD JB shall be mentioned if needed for some cases |  | BK-SUR-ENG-INS-00-01341 | 2021-08-15 | Eexe mentioned as a minimum requirement
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and inculpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 15 Aug 2021 |  |  |  |  | Date: