## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-CN-0005 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0481 |  |  | Transmital Date: 19-Jan-2022
Document Title: Calculation Note for DC Charger System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0010-EL-TR-0481 |  |  | Transmital Date: 19-Jan-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-CN-0005-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1-1 | در بند 3.9، با توجه به اینکه هر بانک باتری 50 درصد بار را برای کل مدت زمان پشتیبانی تامین می کند ، لازم است که محاسبات ، بررسی و اصلاح گردند. |  | 1400-2294-412403 | 1400/11/27 | اعمال گردید.
1-2 | لازم است که تاییدیه لیست بارهای ابزاردقیق به همراه مدرک جهت بررسی به این امور ارسال گردد. |  | 1400-2294-412403 | 1400/11/27 | مطابق با ترنسمیتال 852 که در آن لیست بار بخش ابزاردقیق تولید شده است این مدرک بروز رسانی گردید.
1-3 | در بند 10، در محاسبات جریان شارژر ها، برای سیستم های 24 و 110 ولت، جریان حالت پیوسته (Continuose Dc Load) دو برابر جریان درج شده در جدول بار لحاظ شده است. لازم است دلیل انتخاب این مقادیر اعلام گردد. |  | 1400-2294-412403 | 1400/11/27 | Continuose Dc Load برای دو ست باتری و محاسبه جریان شارژ برای مجموع بار ها در نظر گرفته شده است. به عبارتی دیگر با توجه به اینکه ظرفیت رک های باتری 50 درصد می باشد، این عدد باید دو برابر شده تا بتوان محاسبه ظرفیت شارژر را در نظر گرفت.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: