## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-CN-0011-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0687 |  |  | Transmital Date: 07-Mar-2022
Document Title: Calculation Note For 11 KV Over Head Line Sag and Tension |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0007-EL-TR-0687 |  |  | Transmital Date: 07-Mar-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-CN-0011-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | همانگونه که در مکاتبات قبلی نیز مطرح گردید، در ابتدا لازم است که مسیر پلان و پروفیل خط انتقال برق نهایی و سپس بر اساس این مدارک محاسبات انجام شود، لذا این مدرک در این مقطع زمانی قابل بررسی نیست. مقتضی است پس از تایید مسیر و پلان پروفیل، نسبت به بازنگری این مدرک اقدام و جهت بررسی به این امور ارسال گردد. |  | 00/2294/449000 | 1400/12/23 | احتراما مطابق توضیحات پیشین و همانگونه که مستحضرید محاسبات Sag-Tension پیش نیاز مدرک پلان پروفیل و برج گذاری بوده به نحویکه در این مدرک رفتار هادی در شرایط مختلف بارگذاری تبیین و میزان کشش و فلش و درصد UTS هادی در اسپن های مختلف مشخص شده و سپس بر اساس آن جداول بارگذاری برج ها محاسبه و نهایتا اسپن معادل (اسپن بهینه طراحی) مشخص میگردد تا در پلان پروفیل مورد استفاده قرار گیرد. علاوه بر این مدارک پلان پروفیل و برج گذاری کلیه چاه ها در تجدیدنظر 0 ارائه شده که می تواند توأمان به همراه محاسبات ارائه شده در این مدرک، مورد بررسی و تایید نهایی قرار گیرد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 25-Oct-21 |  |  |  |  | Date: