## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
ELECTRICAL LOAD LIST IN SIAHMAKAN GAS INJECTION
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | EL | LI | 0001 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL LOAD LIST IN SIAHMAKAN GAS INJECTION نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | May.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-708641
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## Revision
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
ELECTRICAL LOAD LIST IN SIAHMAKAN GAS INJECTION
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 5
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | EL | LI | 0001 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 51
2 | X | [7 empty] | 52
3 | X | [7 empty] | 53
4 | X | [7 empty] | 54
5 | X | [7 empty] | 55
6 | [8 empty] | 56
7 | [8 empty] | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## Abb
Service Type:
N : Normal Load
E : Emergency Load
Load Duty:
C : Continuous Load
I : Intermitant Load
S : Stand By Load
LR/FL: Loacked Rotor / Full Load Current
Load Type:
M: Motor
F: Non-Motor
Definition of API Factor
1.25 for Motor Power < 22kW,
1.15 for Motor Power between, 22kW and 55kW
1.1 for Motor Power > 55kW
Height derating factor can be determined as follows if no manufacturer data is available:
Height Above Sea Level | Height Factor
< 1000 m | 1
1000 < Height < 1500 m | 0.97
1500 m > | 0.94
Coolant (Cooling) Factor will be finilized by Electromotors Vendor Datd and before that will be considered :0.88
Feeder Type:
F1: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for I<63A Feeders
تسهیلات
ELECTRICAL LOAD LIST IN SIAHMAKAN GAS INJECTION
شماره صفحه: 3 از 5
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
بستههای کاری تحتالارض
احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
320
EL
LI
0001
D00
بسته کاری
PPL
پروژه
BK

## Calculation
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
ELECTRICAL LOAD LIST IN SIAHMAKAN GAS INJECTION
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 5
9184 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | EL | LI | 0001 | D00
| 1. Mechanical Power (KW): |  | Mechanical Power for Motors = BHP(KW) x API Factor / (Cooling Factor x Height Factor)
| 2. Rated Power(KW): |  | Rated Power = The Nearest Size of The Equipment to Mechanical Power of Motors
| 3. Load Factor(%): |  | Load Factor = (BHP/Rated Power) x 100
| 4. Normal Operation(A): |  | Normal Operation (A) = Rated Power / (Sqrt(3) x Nominal Voltage x cosØ)
| 5. Starting Current(A): |  | Starting Current(A) = (LR/LF) x Normal Current
6. Electrical Power Demand (KW):
Electrical Absorbed Power Demand (KW) = BHP(KW) x Diversity Factor / Efficiency
Electrical Absorbed Power Demand (KW) = Rated Power(KW) x Diversity Factor / Efficiency
7. Electrical Reactive Power Demand (KVAR):
Electrical Reactive Power Demand (KVAR) = Electrical Absorbed Power Demand (KW) x Tangent(Ø
For "Electrical Demand" calculation, following "Diversity Factors" has been considered (based on peak loads):
Continous: 100% Diversity factor.
Intermittent: Normally less than 12 hours/day, As generaly 75%
Standby: Spare/Backup drives or systems, As generaly 10% or biggest standby load (which is bigger)

## PPL
Load List of Well-12
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | Load Duty | Diversity Factor for Demand Load | NO Phases | Rated Voltage (V) | Load Type | Starting Method | BHP (Kw) | API Factor | Coolant Factor | Height Factor | Mechanical Power (Kw) | Rated Power (Kw) | Eff. (%) | Power Factor | Load Factor (%) | LR/FL | Current Normal Operation(A) | Absorbed Peak Active Power (Kw) | Absorbed Peak Reactive Power (Kvar) | Absorbed Peak Apparent Power (KVA) | Feeder Type
1 | D00 | Existing Switchgear in Siahmakan | TR1-F | Rectifier Transformer Cathodic Protection | N | C | 1 | 3 | 0.4 | F | - | - | - | - | - | - | 5 | 90 | 85 | 100 | 1 | 9.4338 | 5.5556 | 3.443 | 6.5359 | F1
تسهیلات
ELECTRICAL LOAD LIST IN SIAHMAKAN GAS INJECTION
شماره صفحه: 5 از 10
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
بستههای کاری تحتالارض
احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
320
EL
LI
0001
D00
بسته کاری
PPL
پروژه
BK