## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-SSGRL-PEDCO-110-ME-DT-0001-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0790 |  |  | Transmital Date: 09/Apr/2022
Document Title: DATA SHEETS FOR FUEL OIL STORAGE DRUM OF WELL PADS |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-ME-TR-0790 |  |  | Transmital Date: 09/Apr/2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-ME-DT-0001-D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
| Test Press. (barg) Per Code & Specification مطابق استاندارد مربوطه محاسبه و اعمال گردد. |  | BK-SUR-ENG-MEC-01-03894 | 2022-04-13 | اعمال گردید
| SA 234 Gr.WPB / SA 105 / SA 106 Gr.B بر اساس ASTM به صورت کامل نوشته شود. |  | BK-SUR-ENG-MEC-01-03894 | 2022-04-13 | بر اساس ASTM نام گذاری به صورت A 105 است که معادل SA 105 در استاندارد ASME II می باشد.
| Anchor Bolts |  | BK-SUR-ENG-MEC-01-03894 | 2022-04-13 | تهیه Anchor bolts بر عهده ی وندور نیست و مطابق نوت 2 تنها سایز کرن آن بر عهده سازنده می باشد.
| L 1,2 => 300# |  | BK-SUR-ENG-MEC-01-03894 | 2022-04-13 | الزام در نظر گرفتن اتصالات با ریتینگ حداقل 300 برای ادوات ابزار دقیق، مربوط به بخش فرایندی میباشد. از آنجا که مخزن دیزل مورد نظربرای مصارف تاسیسات ساختمانی فرض شده است پیشنهاد میشود ریتینگ LG نصب شده برروی آن معادل ریتینگ فشارمخزن (150#) در نظر گرفته شود.
| برای مخزن مقادیر زیر مشخص گردد: LLL / LLLL / HLL / HHLL Fixed / sliding saddle |  | BK-SUR-ENG-MEC-01-03894 | 2022-04-13 | اعمال گردید
| شیب به سمت drain مشخص گردد. (Slope) |  | BK-SUR-ENG-MEC-01-03894 | 2022-04-13 | اعمال گردید
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.Bavarsad | Signature | H.naserizadeh |  |  | Clarified By: H.Adineh | Signature
| Date: 4/13/2022 |  |  |  |  | Date: 6/6/2022