| # | Clarification Title | Clarification Description(Rev.00) | Conclusion (Rev.00) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description(Rev.01) | Conclusion (Rev.01) (VENDOR to Confirm & Consider in the Final Offers) | Clarification Description(Rev.02) | Conclusion (Rev.02) (VENDOR to Confirm & Consider in the Final Offers) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |  |  |
|  | Documents Priority | Vendor to confirm that in case of contradiction between this TCL and offer; vendor confirmation of compliance through this technical clarification is governed and shall be followed by vendor after order. In such case offer won’t be considered as basis of any claim after order. | Confirmed. | Closed |  |  |  |
|  | Deviation List | Bidder shall confirm his full compliance to meet all purchaser documents listed and attached to MR, code / standards listed in MR with ref. No. "BK-GCS-PEDCO-120-ME-MR-0001" as well as MR requirements. All deviations shall be listed in project deviation form, attach to this TCL, signed and stamped. Notes: 1-Any exception and deviation from the requirements of MR and the related specifications including referenced codes & standards shall be clearly declared by vendor in writing for purchaser’s approval at bid stage by using of the format included in “Letter Of Conformity” attached to material requisition. Raising no deviation to any single requirement means full compliance of vendor quotation to that requirement. Purchaser has no responsibility to discover deviations or alternatives scattered over the proposal in addition to what proclaimed explicitly in deviation list; hence such deviation (if any) is disregarded and shall not be considered for vendor claim in future. (Vendor to confirm) 2- Bidder shall confirm that all MR attachments listed in MR are available for her for review at bid stage. 3-Considering items 1 & 2, please note that any deviation at detail stage will not be accepted by purchaser. 4- Please find attached purchaser comments / clarification due to deviations raised by bidder | Confirmed. Confirmed. Confirmed. Confirmed. | Closed |  |  |  |
|  | Documents Priority | Bidder to confirm his compliance with documents priority stated in MR. Any conflict between the documents shall be notified by bidder to purchaser and resolved by his agreement | Some docs mentioned in MR is not in MR attachemt file ,please refer to 0801-JA00846-CDL-0_CLARIFICATION AND DEVIATIONS ON MR. |  |  |  |  |
|  | Requirement For Documents | Bidder to confirm that documents required after purchase order shall be submitted in accordance with “RFD Form” attached to the MR. | Confirmed. | Closed |  |  |  |
|  | Requirement For Documents | Bidder shall provide following documents while bidding: 1- Copy of valid quality system certificate(ISO 9001/2 or 3) 2- Sub- vendors / sub-suppliers list 3- Deviation list with letter of conformity (Refer to item A2 above) 4- Reference and Experience List 5- Joint venture agreement (If any) with any company to design / fabrication of equipment. In case of joint venture ; qualified documents of the company who is part of joint venture shall be also submitted | Added in upgraded technical proposal Added in upgraded technical proposal Not mentioned in MR Added in upgraded technical proposal NA | Closed |  |  |  |
|  | Sub-Vendors | Bidder to confirm that Sub-Vendors shall be selected from Project’s approved AVL. | Please see CST-CST.SBW sub-vendor list. | Not accepted vendor to follow this requirement | We didn’t find project AVL, please send it to us . |  |  |
|  | Specification | Bidder to confirm that surface preparation and painting of all equipment material including valves , pipes , fittings and everything within the package are in accordance with the project painting specification attached to MR. | Confirmed. | Closed |  |  |  |
|  | Specification | Bidder to confirm that Packing, Marking, Preservation and Preparation for Shipment will be done in accordance to the project specification attached to the MR. | Confirmed. | Closed |  |  |  |
|  | Inspection and Test Plan | Inspection and Test Plan / Quality Control Plan and their related inspection level (Witness, Hold, Review and Approval) shall be at least in accordance with MR and all project requirement such as project ITP and “QA inspection and test” section of datasheets. Any deviation is not accepted unless otherwise specified in deviation list and approved by Purchaser. | Confirmed. | Closed |  |  |  |
|  | Material Certificate | Bidder to confirm that for all pressure parts and those required special consideration or stainless steel as well as for supports the material certificate should be in accordance with EN 10204, 3.1 Material certificate for non-pressure parts shall be in accordance with EN 10204, 2.2. | Confirmed. | Closed |  |  |  |
|  | Scope | Bidder shall confirm the scope of work and supply are fully in accordance with MR and its attachment with following items: 1- The consequences of HAZOP and SIL study shall be in vendor scope of supply and work. 2- Participation in technical meeting whenever it is necessary by Purchaser/Client to close engineering document after order is in vendor scope 3- Lifting beams (Spreader beams) for erection with sling shackle and etc. shall be designed and supplied by vendor 4- N2 preservation with pressure regulator, valve & flexible hoses during transportation & 18 months of site storage based on requirements in MR shall be in vendor scope of supply / work. 5- All utility conditions shall be as per document "Process basis of Design Document; Doc. No: BK-GNRAL-PEDCO-000-PR-DB-0001". Moreover bidder shall consider utility noted condition as per project design data. If other utility condition is needed, whole required facilities is in vendor scope of work/supply. 6- Anchor bolts | 1.Confirmed. 2.Confirmed. 3.Confirmed- if required. 4.Confirmed. 5.Confirmed. 6.Confirmed. | 3- To be provided by vendor. But Noted for other items. | 3-No need due to non-skided compressor. |  |  |
|  | Notice | Everywhere vendor used “Noted” or “Enclosed” it will be assumed as “Confirmed”. | Confirmed. | Closed |  |  |  |
|  | Spare Part | Vendor shall supply his spare parts as per the attached spare part list (as minimum): | CST-CST.SBW can’t click this attachment. Please see spare part list in technical proposal which is received recently. | Closed |  |  |  |
| - PROCESS |  |  |  |  |  |  |  |
|  | General Unit Description | There are not cooling water in site | Noted. Cooling water console is air cooled. Cylinder , packing and lube oil console is cooled by water supplied by cooling water console tank. |  |  |  |  |
|  | Compressor | Mechanical data sheet shall be revised based on latest revision of process data sheet. vendor proposal shall be revised base on last revision of compressor data sheet. | Upgraded. |  |  |  |  |
|  | Allowable Particle Size | please specified maximum acceptable liquid particle in suction nozzle of compressor | Maximum acceptable liquid particle is 20 micron through the separator or strainer. |  |  |  |  |
|  | Utilities (preliminary) | instrument air consumption for compressor package shall be specified (if required) | Added |  |  |  |  |
|  | Utilities (preliminary) | Please explain the purpose of intermittent nitrogen consumption | For cooling water tank ,Prevents leakage of process gas to the environment after packing leaks |  |  |  |  |
|  | P and ID | Please submitted P& id of spill back system for each train. Spill back valve to be supplied by vendor and the logic for its control to be considered in the compressor’s UCP. Position transmitter/limit switch to be provided by vendor. | Added. |  |  |  |  |
|  | MDMT | Vendor shall confirm to select a proper material for MDMT equal to -26 degC. | Confirmed. |  |  |  |  |
|  | General Unit Description | Ambient Conditions shall be revised based on latest revision of Process Basis of Design | Confirmed. |  |  |  |  |
|  | Utilities | NITROGEN purity shall be considered 98 % VOL MAX | Confirmed. |  |  |  |  |
|  | Proposal pdf file; Compressor package description - General |  |  | Please specify compressor efficiency | Added. |  |  |
|  | Proposal pdf file; Cooling water console |  |  | One for each compressor to be considered by vendor | Confirmed. |  |  |
|  | Proposal pdf file; Utility consumption list; DMW requirement |  |  | Please specify service water. Specification is suitable for compressor cooling water system. Please Specify Inlet Temp, Inlet Pressure of utility Items. | Added in 0401-JA00846-UCL_UTILITY CONSUMPTION LIST |  |  |
|  | Proposal pdf file; Process gas P&ID; 1st stage process gas inlet |  |  | Please clarify the strainer is by vendor or contractor ? | By CST.SBW. |  |  |
|  | Process Comments |  |  | For Process comments refer to Attachment#2 of this TCL. | Upgraded and attached doc for reply. |  |  |
|  | Process comments |  |  |  |  | For process comments refer to Attachment#2 of this TCL. |  |
| - MECHANIC |  |  |  |  |  |  |  |
|  | Document Requirement | Bidder to submit all required documents with tender as per “RFD Form” in the MR. For example below documents: 1-Marked up and Filled out MR scope of supply and works (It shall be signed and stamped) 2-Performance curves and tables 3-GA DWG with outline dimensions and weights related to this project 4-Sectional DWG. with BOM 5-Noise Data 6-Utility Consumption List | - Added. - It will be submit after PO - Added. - It will be submit after PO - It will be submit after PO - Added. | - Noted - Noted - Noted - Noted, If vendor confirm to follow all purchaser’s comment after P.O. - Noted, If vendor confirm to follow all purchaser’s comment after P.O. | 4-Confirmed. 5-Confirmed. |  |  |
|  | Material | ASTM number and grade of all supplied material to be specified in next revision offer. Some material to be changed in next revision offer, related ASTM No. to be provided in next revision offer. | Please refer to compressor datasheet | Closed |  |  |  |
|  | Applied Standards | Applied Standards for equipment design, fabrication and test shall be listed | Added. | Closed |  |  |  |
|  | Design Standards | Design standard of coupling shall be API 671 4th edition flexible disk type. Coupling model, material, balance grade and spacer length to be specified at this stge. API 671 data sheet shall be filled out and submitted after order. API671 dry flexible metallic disk with spacer with balancing grade G.2.5 to be used. | NA, CST-CST.SBW will supply rigid connection without coupling. | Not accepted, Vendor to follow this requirement | Confirmed. |  |  |
|  | Vendor’s Scope | Design and supplying Heat Tracing and insulation if required to be in the vendor’s scope. Vendor shall follow this requirement | Confirmed (CST) | Closed |  |  |  |
|  | Vendor’s Scope | All vents and drains of the package to be valved, manifolded and to be routed to the edge of skid. | Confirmed. | Closed |  |  |  |
|  | Inspection and Test | Test procedures and acceptance criteria will be checked after order with project specifications and related standards. Vendor to confirm to follow project standard and spec. | Confirmed. | Closed |  |  |  |
|  | Comments on Vendor’s Proposal and its attachments | Please refer to the Attachment #1 of this TCL for Mechanical comments on the offer. | We didn’t find att. #1, please resend | Closed |  |  |  |
|  | Guarantee | Vendor shall guarantee his design that in case of power failure, the bearing and the machine will be protected during coast down period | Confirmed. | Closed |  |  |  |
|  | Compressor mechanical data sheet |  |  | Compressor mechanical data sheet revised based on latest revision of process data sheet. (refer to Attachment#1 of this TCL for rev. D06 of MDS). Vendor shall revise his offer according to new MDS. | Upgraded. |  |  |
|  | NEW ITEM |  |  | Split of work and supply between CST and CST.SBW to be specified in next revision offer. | enclosed |  |  |
| - PIPING & MATERIAL |  |  |  |  |  |  |  |
|  | Compressor P&ID | Tag of Compressor in vendor P&ID to be modified according to Project tags (C-2101 & C-2102). | Confirmed. | Noted and Closed. |  |  |  |
|  | Compressor P&ID | Name of all Auxiliary Skids to be specified in all sheets of P&ID. Piping between all Compressor skids are in scope of work of Compressor vendor and it shall be modified in P&ID. | See revised PID based on new CST-CST.SBW JV | Noted and Closed. |  |  |  |
|  | Compressor Stages Arrangement | Location of 1st Stage & 2nd Stage of Compressor and their Inlet & Outlet nozzles shall be shown in Compressor G.A Drawing. Due to arrangement of Suction Drums & Air Coolers in scope of Client, Location of 1st Stage of Compressor shall be in Left side of Compressor Package from Front View direction in Compressor G.A Drawing and 2nd Stage of Compressor in Right side. | Added. | Noted and Closed. |  |  |  |
|  | Compressor Auxiliary Skids | Name of Auxiliary Skids to be specified in G.A. drawing and their distances from main Compressor Skid. Distances will be finalized after P.O. when receiving vendor Detail Drawings. | Confirmed. | Noted and Closed. |  |  |  |
|  | Compressor Package Scope of supply | Piping between all Compressor skids are in scope of work of Compressor vendor and it shall be mentioned in Technical Proposal document. | Confirmed. | Noted and Closed. |  |  |  |
|  | Compressor Data Sheet | In page 49 of vendor Technical Proposal, According to Project P&ID, size of Discharge line of 2nd Stage is 6". | Confirmed. | Noted and Closed. |  |  |  |
|  | Compressor Piping Stress Analysis | Pulsation and vibration study shall be performed by vendor (according to 2.17). Vendor shall locate Tie-in points in positions where pulsation and vibration do not affect purchaser side's piping. Tie-in point has zero displacement and rotation, otherwise displacements shall be specified by vendor at this tie-in point. In the event that pulsation study result has impact on purchaser piping routes and/or pipe supports, all vendor requirements shall be informed to purchaser by marking-up pipe route clearly. Since space management and piping static stress analysis are in purchaser scope of work, vendor to obtain purchaser approval on marked-up isometric drawings. | Confirmed. |  |  | Closed |  |
|  | Compressor Piping Stress Analysis | Vendor shall provide allowable piping loads at the tie-in points. Allowable nozzle loads shall be in accordance with "Appendix N in Specification For Pressure Vessels". In case of unavoidable over loaded, then the loads should be submitted to the vendor for consideration and approval. (Mentioned in the Data Sheet) | Confirmed. |  |  | Closed |  |
|  | Compressor Material | New Comment: Material requirement shall be in compliance with NACE MR 0175/ISO 15156 and Specification for Material Requirements in Sour service BK-GNRAL-PEDCO-000-PI-SP-0008. | Confirmed. |  |  | Closed |  |
| INSTRUMENT & CONTROL |  |  |  |  |  |  |  |
|  | Control System Requirements | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0004 and provide the requirement of type C package as mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. 1-One UCP with redundant CPU dedicated for all train to be provided by vendor. 2-SIL rated loops for protection and trip to be merged inside UCP panel. 3- Monitoring of machine protection signals could be also merged inside UCP panel due to vendor design (required transmitters/transducer for temperature/vibration and etc. sensors to be considered for UCP connection otherwise separate panel, at least VMS to be provided. ) 4-Loose instruments as per purchaser’s P&ID and also spill back valve is in vendor’s scope of supply Special cables (if any) shall be supplied by vendor. 5-All original software and licenses, workstation and laptops as per project documents to be considered by vendor | - CST-CST.SBW will supply one UCP common for 3 compressors; please confirm the Suitability. - Confirmed. - Confirmed. - Confirmed. - CST-CST.SBW will supply one workstation and one laptop common for 3 compressors; Please confirm the suitability | To be implemented on package UCP Control block diagram. Modbus link between DCS and UCP to be confirmed. | Added in 0581-JA17151-DIG_CONTROL SYSTEM CONFIGURATION. |  |  |
|  | Panel Requirements | VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0002,0003 for panels mounted in control building and field panels and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Confirmed. | Closed. |  |  |  |
|  | Instrumentation | Regarding supplying instrument on datasheet), bidder is requested to consider all instruments mentioned on project datasheet. VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0001 for instrumentation devices and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. Vendor shall confirm to follow this requirement for all instrument inside the package and also all loosed instrument as per project P&ID. (marked with V and VF) For loose Instrument manifold shall be provided by vendor, other hook up/installation requirement will be provided by contractor. | Confirmed. | Closed. |  |  |  |
|  | Instrumentation Valves | VENDOR shall follow below documents for valves and other documents as mentioned in these documents. - BK-GNRAL-PEDCO-000-IN-SP-0005 - BK-GNRAL-PEDCO-000-IN-SP-0006 - BK-GNRAL-PEDCO-000-IN-SP-0007 VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. | Confirmed. | Closed. |  |  |  |
|  | Cable | - VENDOR shall follow BK-GNRAL-PEDCO-000-IN-SP-0010 for cables and all other details mentioned in this document. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. Special cables (if any) shall be supplied by vendor. | Confirmed. | Closed. |  |  |  |
|  | Terminals | All terminals shall be screw type. VENDOR shall note that each core/pair/etc. of cable shall be wired to dedicated terminal | Confirmed. | Closed. |  |  |  |
|  | Panel Dimension | VENDOR shall specify the estimated number and dimension of panels. Befor PO it shall be specified | It will be specified after PO. | To be Specified by vendor to meet control room free space. | Confirmed. |  |  |
|  | Required Power | VENDOR shall specify the estimated power required (non-UPS and UPS) Befor PO it shall be specified | Estimated power required :4 kW | Closed. |  |  |  |
|  | Special Tools | VENDOR shall supply all special tools for compressor and axillary devices. This is included the special cables (not mentioned in BK-GNRAL-PEDCO-000-IN-SP-0010), MODBUS sockets, software and etc. The list shall be provided separately. | Added. | Closed. |  |  |  |
|  | Protection Instruments | The protective instruments shall be according to API-670. VENDOR shall comply with all the requirements and mentioned any mismatch in deviation list which is attached to the PMR. This requirement shall be followed by vendor also API670 figure H.6 shall be followed by him. | Added. | Closed. |  |  |  |
|  | Software | VENDOR shall supply all the software (including the passwords, licenses and program sources). The programs shall be supplied with all tags, descriptions and etc. The software programs shall be installed on engineering laptops and also supplied on CD/DVD. | Confirmed. | Closed. |  |  |  |
|  | Load Sharing | VENDOR shall clearly specify the scenario for load sharing. The interface signals, required hardware (e.g. panels, if any) and additional control or on/off valves. | Confirmed. | Closed. |  |  |  |
|  | Start-up | VENDOR shall clearly state the start-up sequence. It shall be mentioned if any additional instrument or valve is required. Also, the interface signals shall be mentioned (if any) | Confirmed. | Closed. |  |  |  |
|  | Other comments | For other instrument comments refer to attached file as following: | Upgraded. | See attached comments. Refer to Instrument comments on tech proposal pdf file. (Attachment#2 of TCL ATTACHMENT) | Please see attached doc. For CST.SBW reply. |  |  |
| SAFETY |  |  |  |  |  |  |  |
|  | Noise level | Vendor to confirm that Noise level @1m should be 85 dbA. | Confirmed. |  |  |  |  |
|  | Area Classification | Electrical devices should be certified for Zone 2 Gas group IIB, T3. | Confirmed. |  |  |  |  |
| ELECTRICAL |  |  |  |  |  |  |  |
|  | Vendor Scope of Work | Electrical system scope of work shall be clarified by vendor & any deviation shall be reported. | Please refer to SOW in technical proposal. | Closed |  |  |  |
|  | Vendor Scope of Work | All documents related to electrical equipment should be submitted by vendor such as electrical motor data sheet, motor outline drawing & etc. | They will be submitted after PO. | Closed |  |  |  |
|  | Vendor Scope of Work | Vendor list & sub vendor list of manufacture shall be according to project AVL. | Since there are Sanction limitation and un-availability for Iran’s market; Please refer to CST-CST.SBW sub-vendor list in technical proposal. This issue is subjected to clarification and approval by client. | Closed |  |  |  |
|  | Specification | All electrical equipment shall comply with electrical references & standard that mentioned on material requisition. (IPS-M-EL-131 (2) & IPS-M-EL-132 (2)) | Confirmed. | Closed |  |  |  |
|  | Specification | Motor shall be manufactured & tested in accordance with the latest applicable sections of the IEC standards. Project specification shall be applied as well. | Confirmed. | Closed |  |  |  |
|  | Specification | Environmental criteria for design of electrical systems that shall be considered by vendor (According to Electrical System Design Criteria) | Confirmed. | Closed |  |  |  |
|  | Specification | Hazard Area classification, Gas group and temperature class of motor shall be at least Exd, IIB, T3, with protection degree of IP54 for motor enclosure and IP55 for terminal box. (See section 2.2 of compressor driver) | Confirmed. | Closed |  |  |  |
|  | Data Sheet | - 1. Anti-condensation heaters shall be provided for all medium voltage & high voltage motors. - 2.The voltage of anti-condensation heaters shall be 230 v single phase for heaters up to 3 Kw. For heaters above 3 kw, 400v three phase & neutral shall be used. - 3.The anti-condensation heaters shall be wired to a separate terminal box mounted on the motor frame. | - Confirmed. - Confirmed. - Confirmed. | Closed |  |  |  |
|  | Vendor Scope of Work | Local control station/panel for electrical equipment should be supply by vendor. It shall be according to “BK-GCS-PEDCO-120-EL-DT-0006” | We didn’t find BK-GCS-PEDCO-120-EL-DT-0006 in MR. | It will be attached in next revision by client. | Confirmed. |  |  |
|  | Vendor Scope of Work | All accessories related to cable entry/termination in electrical equipment (motors, JBs, etc.) such as cable glands & etc. shall be supplied by vendor. | Confirmed. | Closed |  |  |  |
|  | Specification | 2 temperature detector (RTD) for each winding & 1 one RTD for each bearing should be provided for MV motor | Confirmed. | Closed |  |  |  |
|  | Specification | Differential protection current transformer shall be provided for motors above 1000 Kw. | Confirmed. | Closed |  |  |  |
|  | Load List | Electrical load list of motor include Mechanical power (BHP), Rated power, efficiency, power factor and rated current shall be specified in the proposal. | It will be submit after PO. | Closed |  |  |  |
|  | Load List | API factor, effect of ambient condition especially de-rate factor for altitude shall be considered for specifying rated power of motor and procedure of obtaining rated power of motor from BHP shall be cleared in the proposal. | Confirmed. | Closed |  |  |  |
|  | Specification | Compressor motors, shall be 11 Kv & 50 Hz. (Please check page 4 & 15 of TCL) LV motors rated up to 150 Kw, shall be 0.4 Kv & 50 Hz. All motors shall be capable of operating continuously at rated torque at any frequency between -2% & +2% with voltage variation of ±5%. | Confirmed. | Closed |  |  |  |
|  | Data Sheet | Insulation class shall be F and temperature rise shall be B. | Confirmed. | Closed |  |  |  |
|  | Spare Part | A complete set of spare parts for commissioning shall be supplied for each motor. | We didn’t find motor spare parts list in MR, please inform us it. | It is as an attachment in MR. | Upgraded in 0301-JA00846-SPL_SPARE PART LIST |  |  |
|  | Test & Inspection | The equipment shall be factory tested. Certified copies of test reports shall be submitted to the purchaser. | Confirmed. | Closed |  |  |  |
|  | Data Sheet (Pg 13 of technical Offer) | In electrical service item, electrical data for auxiliary pumps of compressor shall be specified by vendor in data sheet. | It will be submit after PO. | Closed |  |  |  |
|  | Data Sheet | Electrical data sheet “BK-GCS-PEDCO-120-EL-DT-0009” shall be completed by vendor. | It will be submit after PO. | Closed |  |  |  |
|  | Vendor Scope of Work | Supplier shall design the routing of the power & control cable inside package. | Confirmed. | Closed |  |  |  |
|  | Vendor Scope of Work | - Supply of cables between Junction boxes and Package control panel is in vendor scope of work. In other word, All cabling listed in “Customer cable table” shall be supplied and connected by customer/contractor. - Cables shall be according to “BK-GNRAL-PEDCO-000-EL-SP-0014”. | cable between junction boxes and package control panel (UCP) is not in scope of CST-CST.SBW supply.. | Closed |  |  |  |
|  | Vendor Scope of Work | If UPS & batteries are required, vendor shall provide all necessary documents (such as calculation, list etc.) & supply required equipment according to purchaser standards. | Confirmed. | Closed |  |  |  |
|  | Specification | Glands shall be of threaded type or fitted in equally strong way | Confirmed. | Closed |  |  |  |
|  | TCL File | According to TCL file, it seems there is not any deviation. Please confirm. | Please see deviation in technical proposal. | Closed |  |  |  |
|  | Technical offer | In section 2.11 of page 11, open conduit in hazardous area is not acceptable. Please check. | Deleted. | Closed |  |  |  |
|  | Technical offer | In page 16 of Technical offer, (Utility Consumption), the heater for main motor has not been considered. Please check. | Added. | Closed |  |  |  |
|  | Vendor Scope of Work |  |  | Power demand for Auxiliary consumption of each compressor will be supplied by client. |  | Power demand for Auxiliary consumption of each compressor will be supplied by client. But SLD of this auxiliary panel & interconnection with UCP shall be issued by vendor. this item to be clarified by vendor. |  |