## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 58
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | LI | 0009 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT / F&G CABLE LIST نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | JUN.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | FEB.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | Client Approval
Class: 2 |  |  |  | Client Doc. Number: F0Z-708975
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for Client Review
AB-A: As-Built –Approved

## Revisions
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 58
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | LI | 0009 |  | D01
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 | X | X | [6 empty] | 71
8 | X | X | [6 empty] | 72
9 | X | X | [6 empty] | 73
10 | X | X | [6 empty] | 74
11 | X | X | [6 empty] | 75
12 | X | X | [6 empty] | 76
13 | X | X | [6 empty] | 77
14 | X | X | [6 empty] | 78
15 | X | X | [6 empty] | 79
16 | X | X | [6 empty] | 80
17 | X | X | [6 empty] | 81
18 | X | X | [6 empty] | 82
19 | X | X | [6 empty] | 83
20 | X | X | [6 empty] | 84
21 | X | X | [6 empty] | 85
22 | X | X | [6 empty] | 86
23 | X | X | [6 empty] | 87
24 | X | X | [6 empty] | 88
25 | X | X | [6 empty] | 89
26 | X | X | [6 empty] | 90
27 | X | X | [6 empty] | 91
28 | X | X | [6 empty] | 92
29 | X | X | [6 empty] | 93
30 | X | X | [6 empty] | 94
31 | X | X | [6 empty] | 95
32 | X | X | [6 empty] | 96
33 | X | X | [6 empty] | 97
34 | X | X | [6 empty] | 98
35 | X | X | [6 empty] | 99
36 | X | X | [6 empty] | 100
37 | X | X | [6 empty] | 101
38 | X | X | [6 empty] | 102
39 | X | X | [6 empty] | 103
40 | X | X | [6 empty] | 104
41 | X | X | [6 empty] | 105
42 | X | X | [6 empty] | 106
43 | X | X | [6 empty] | 107
44 | X | X | [6 empty] | 108
45 | X | X | [6 empty] | 109
46 | X | X | [6 empty] | 110
47 | X | X | [6 empty] | 111
48 | X | X | [6 empty] | 112
49 | X | X | [6 empty] | 113
50 | X | X | [6 empty] | 114
51 | X | X | [6 empty] | 115
52 | X | X | [6 empty] | 116
53 | X | X | [6 empty] | 117
54 | X | X | [6 empty] | 118
55 | X | X | [6 empty] | 119
56 | X | X | [6 empty] | 120
57 | X | X | [6 empty] | 121
58 | X | X | [6 empty] | 122
59 | X | [7 empty] | 123
60 | X | [7 empty] | 124
61 | X | [7 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Notes & References
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 3 از 58
9184 – 073 - 053 |  |  |  | BK |  | GCS |  | PEDCO | 120 | IN | LI |  | 0009 | D01
GENERAL NOTES:
1- Cable length will be finalized after approval of Instrument location.
2- Gland Size will be finalized after Instrument Cable/Cable Gland P.O
3- Cutting column/Drum no. will be finalized after cable P.O.
4- All cables shall be accordance with Flame retardant standard IEC 60332
5- Fire Resistant cables shall be accordance with standard IEC 60331.
6- All conductors shall be accordance with standard IEC 60228 and the material shall be Tinned cupper.
7- Outer sheath Material :
Flame Retardant : PVC , Color : Light Blue for I.S. & Gray for N.I.S
Fire Resistant : PVC , Color : Light Blue with Red Strip for I.S. & Gray with Red Strip for N.I.S & Red for F&G
[6 empty] | 8- Cable type legend : | [9 empty] | 9- Junction Box Numbering : :
[5 empty] | X - X X - X - X | [9 empty] | JBX - X - XXXX
| BL: Light Blue | [8 empty] | F: Fire resistance | [6 empty] | Sequence No.
| BR: Light Blue/Red Strip | [8 empty] | FA: Fire resistance, Armoured
| GY: Gray | [8 empty] | A: Armoured | [6 empty] | A : Analoge
| GR: Gray /Red Strip | [8 empty] | N: None | [6 empty] | D : Digital
| RD: Red | [15 empty] | S : Solenoid
D : DCS
| Number of core | [15 empty] | E : ESD
| or pair or triad | [10 empty] | 1: 1 mm² |  |  |  |  | F : F&G
2: 1.5 mm²
3: 2.5 mm²
[7 empty] | P: Pair |  |  |  |  | 4: 6 mm²
[7 empty] | C: Core |  |  |  |  | 5: 16 mm²
[7 empty] | T: Triad |  |  |  |  | 6: 35 mm²
REFERENCES:
| 1. | BK-GCS-PEDCO-120-IN-LI-0002_D01 IO LIST FOR CONTROL SYSTEM
| 2 | BK-GCS-PEDCO-120-IN-LI-0003_D01 IO LIST FOR ESD SYSTEM
| 3. | BK-GCS-PEDCO-120-IN-LI-0004_D01 IO LIST FOR F&G SYSTEM
| 4 | BK-GNRAL-PEDCO-000-IN-SP-0010-D00 SPECIFICATION FOR INSTRUMENT & F&G CABLES
| 5 | BK-GCS-PEDCO-120-IN-DG-0008_D01 NSTRUMENT & F&G JUNCTION BOX TERMINATION DIAGRAM
ABBREVIATION :
| 1- CU |  | : Conductor (Standard tinned copper)
| 2- XLPE |  | : Insulation (Cross-linked polyethylene, low smoke, zero halogen)
| 3- DW |  | : Drain Wire
| 4- ISC |  | : Individual Screen
| 5- DW |  | : Drain Wire
| 6- OSC |  | : Overall Screen
| 7- PVC |  | : Inner sheath (polyvinyl chloride insulation )
| 8- SWB |  | : Armoure (Steel wire Braided )
| 9- PVC |  | : Outer sheath (polyvinyl chloride insulation)
| 10- FRT |  | : Flame Retardant
| 11- FRS |  | : Fire Resistant
D01

## SUMMARY
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / F&G CABLE LIST
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 58
9184 – 073 - 053 |  | BK | GAS | PEDCO | 120 | IN | LI | 0009 | D01
SUMMARY
ITEM | TYPE | DESCRIPTION | [6 empty] | QUANTITY (m)(NOTE1)
[9 empty] | ACTUAL (m) |  | (PLUS 20%) (m)
1 | BL-1P-2-A | 1 PAIR * 1.5 mm² , CU/XLPE/DW/ISC/PVC/SWB/PVC, Flame Retardant (IEC-60332) , L.T Blue | [6 empty] | 2160 |  | 2592
2 | BL-7P-1-A | 7 PAIR * 1 mm² , CU/XLPE/DW/ISC/DW/OSC/PVC/SWB/PVC, Flame Retardant (IEC-60332) , L.T Blue | [6 empty] | 990 |  | 1188
3 | BL-12P-1-A | 12 PAIR * 1 mm² , CU/XLPE/DW/ISC/DW/OSC/PVC/SWB/PVC, Flame Retardant (IEC-60332) , L.T Blue | [6 empty] | 4580 |  | 5496
4 | GY-1P-2-A | 1 PAIR * 1.5 mm² , CU/XLPE/DW/ISC/PVC/SWB/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 420 |  | 504
5 | GY-7P-1 | 7 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 300 |  | 360
6 | GY-7P-1-A | 7 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC/SWB/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 2240 |  | 2688
7 | GY-12P-1-A | 12 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC/SWB/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 2490 |  | 2988
8 | GY-20P-1-A | 20 PAIR * 1 mm² , CU/XLPE/DW/OSC/PVC/SWB/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 450 |  | 540
9 | GY-1P-3-A | 1 PAIR * 2.5 mm² , CU/XLPE/DW/ISC/PVC/SWB/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 165 |  | 198
10 | GY-7P-3-A | 7 PAIR * 2.5 mm² , CU/XLPE/DW/OSC/PVC/SWB/PVC, Flame Retardant (IEC-60332) , Gray | [6 empty] | 1340 |  | 1608
11 | BR-1P-2-FA | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-LT. Blue / Red Strip | [6 empty] | 1790 |  | 2148
12 | BR-7P-1-FA | 7 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-LT. Blue / Red Strip | [6 empty] | 1810 |  | 2172
13 | BR-12P-1-FA | 12 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-LT. Blue / Red Strip | [6 empty] | 2120 |  | 2544
14 | GR-1P-2-FA | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 360 |  | 432
15 | GR-20P-1-F | 20 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 100 |  | 120
16 | GR-20P-1-FA | 20 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 100 |  | 120
17 | GR-7P-1-F | 7 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 350 |  | 420
18 | GR-7P-1-FA | 7 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 2510 |  | 3012
19 | GR-1P-3-FA | 1 PAIR * 2.5 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 790 |  | 948
20 | GR-7P-3-FA | 7 PAIR * 2.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-Gray / Red Strip | [6 empty] | 3030 |  | 3636
21 | RD-1P-2-F | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 635 |  | 762
22 | RD-1P-2-FA | 1 PAIR * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 915 |  | 1098
23 | RD-7P-1-F | 7 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 100 |  | 120
24 | RD-7P-1-FA | 7 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 2620 |  | 3144
25 | RD-12P-1-FA | 12 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 920 |  | 1104
26 | RD-20P-1-F | 20 PAIR * 1 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 100 |  | 120
27 | RD-1T-2-FA | 1 Traid * 1.5 mm² , CU/Mica-tape/XLPE/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 1775 |  | 2130
28 | RD-12T-1-FA | 12 Traid * 1 mm² , CU/Mica-tape/XLPE/DW/ISC/DW/OSC/PVC/SWB/PVC, Fire resistant (IEC-60331)-RED | [6 empty] | 4870 |  | 5844
29 | SERIAL LINK | BY VENDOR | [6 empty] | 100 |  | 120
D01

## Cable list
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
INSTRUMENT / FGS CABLE LIST
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  |  |  | BK | GAS | PEDCO | 120 |  | IN |  | LI | 0009 | D01
ITEM | Cable Code | Tag No. | Description |  | Cable No. | From | To. | FRT OR FRS | ARMOURE TYPE | IS OR NIS | Qty. OF PAIR/ TRIPLE/Core/QUAD | CONDUCTOR TYPE | CONDUCTOR SIZE ( mm2) | SCREENING | OUTER SHEATH COLOR | DRUM No. | INSULATION RATED VOLTAG | CABLE LENGTH (M) | GLAND SIZE | Remark
1 | BL-1P-2-A | FIT-2101 | Flow Transmitter | IC- | FIT-2101 | FIT-2101 | JBD-A-2101 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
2 | BL-1P-2-A | TIT-2102 | Temperature Traansmitter | IC- | TIT-2102 | TIT-2102 | JBD-A-2101 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
3 | BL-1P-2-A | PIT-2102 | Pressure Transmitter | IC- | PIT-2102 | PIT-2102 | JBD-A-2101 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
4 | BL-1P-2-A | FCV-2101 | Flow Control Valve | IC- | FCV-2101 | FCV-2101 | JBD-A-2101 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
5 | BL-7P-1-A | JBD-A-2101 | Junction Box | MC- | JBD-A-2101 | JBD-A-2101 | DCS | FRT | SWA | IS | 7 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 300 | M32
6 | BL-1P-2-A | PI-2103 | Pressure Indicator | IC- | PI-2103 | PI-2103 | JBD-A-2102 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
7 | BL-1P-2-A | TI-2103 | Temperature Indicator | IC- | TI-2103 | TI-2103 | JBD-A-2102 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
8 | BL-1P-2-A | FIT-2102 | Flow Transmitter | IC- | FIT-2102 | FIT-2102 | JBD-A-2102 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
9 | BL-1P-2-A | TIT-2104 | Temperature Transmitter | IC- | TIT-2104 | TIT-2104 | JBD-A-2102 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
10 | BL-1P-2-A | PIT-2104 | Pressure Transmitter | IC- | PIT-2104 | PIT-2104 | JBD-A-2102 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
11 | BL-1P-2-A | FCV-2102 | Flow Control Valve | IC- | FCV-2102 | FCV-2102 | JBD-A-2102 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
12 | BL-1P-2-A | ZA-2102A | PIG Signaller | IC- | ZA-2102A | ZA-2102A | JBD-A-2102 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
13 | BL-1P-2-A | ZA-2102B | PIG Signaller | IC- | ZA-2102B | ZA-2102B | JBD-A-2102 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
14 | BL-12P-1-A | JBD-A-2102 | Junction Box | MC- | JBD-A-2102 | JBD-A-2102 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 300 | M40
15 | BL-1P-2-A | TIT-2111 | Temperature Transmitter | IC- | TIT-2111 | TIT-2111 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
16 | BL-1P-2-A | PIT-2112 | Pressure Indicator Transmitter | IC- | PIT-2112 | PIT-2112 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
17 | BL-1P-2-A | PDIT-2111 | Diff. Pressure Indicator Transmitter | IC- | PDIT-2111 | PDIT-2111 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
18 | BL-1P-2-A | LIT-2111 | Level Indicator Transmitter | IC- | LIT-2111 | LIT-2111 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
19 | BL-1P-2-A | LCV-2111 | Level Control Valve | IC- | LCV-2111 | LCV-2111 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
20 | BL-1P-2-A | LIT-2113 | Level Indicator Transmitter | IC- | LIT-2113 | LIT-2113 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
21 | BL-1P-2-A | LIT-2114 | Level Indicator Transmitter | IC- | LIT-2114 | LIT-2114 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
22 | BL-1P-2-A | PIT-2113 | Pressure Indicator Transmitter | IC- | PIT-2113 | PIT-2113 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
23 | BL-1P-2-A | PIT-2272 | Pressure Indicator Transmitter | IC- | PIT-2272 | PIT-2272 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
24 | BL-1P-2-A | PCV-2272 | Pressure Control Valve | IC- | PCV-2272 | PCV-2272 | JBD-A-2103 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
25 | BL-12P-1-A | JBD-A-2103 | Junction Box | MC- | JBD-A-2103 | JBD-A-2103 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 250 | M40
26 | BL-1P-2-A | FIT-2111 | Flow Indicator Transmitter | IC- | FIT-2111 | FIT-2111 | JBD-A-2104 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
27 | BL-1P-2-A | FCV-2111 | Flow Control Valve | IC- | FCV-2111 | FCV-2111 | JBD-A-2104 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
28 | BL-1P-2-A | PIT-2114 | Pressure Indicator Transmitter | IC- | PIT-2114 | PIT-2114 | JBD-A-2104 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
29 | BL-1P-2-A | FIT-2112A | Flow Indicator Transmitter | IC- | FIT-2112A | FIT-2112A | JBD-A-1004 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
30 | BL-1P-2-A | FCV-2112A | Flow Control Valve | IC- | FCV-2112A | FCV-2112A | JBD-A-1004 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
31 | BL-1P-2-A | FIT-2112B | Flow Indicator Transmitter | IC- | FIT-2112B | FIT-2112B | JBD-A-1004 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
32 | BL-1P-2-A | FCV-2112B | Flow Control Valve | IC- | FCV-2112B | FCV-2112B | JBD-A-1004 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
33 | BL-7P-1-A | JBD-A-2104 | Junction Box | MC- | JBD-A-2104 | JBD-A-2104 | DCS | FRT | SWA | IS | 7 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 270 | M32
34 | BL-1P-2-A | TIT-2112 | Temperature Indicator Transmitter | IC- | TIT-2112 | TIT-2112 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
35 | BL-1P-2-A | PIT-2117 | Pressure Indicator Transmitter | IC- | PIT-2117 | PIT-2117 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
36 | BL-1P-2-A | PDIT-2112 | Diff. Pressure Indicator Transmitter | IC- | PDIT-2112 | PDIT-2112 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
37 | BL-1P-2-A | LIT-2116 | Level Indicator Transmitter | IC- | LIT-2116 | LIT-2116 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
38 | BL-1P-2-A | LIT-2119 | Level Indicator Transmitter | IC- | LIT-2119 | LIT-2119 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
39 | BL-1P-2-A | LCV-2114 | Level Control Valve | IC- | LCV-2114 | LCV-2114 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
40 | BL-1P-2-A | PCV-2271A | Pressure Control Valve | IC- | PCV-2271A | PCV-2271A | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
41 | BL-1P-2-A | PCV-2271B | Pressure Control Valve | IC- | PCV-2271B | PCV-2271B | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
42 | BL-1P-2-A | LIT-2271 | Level Indicator Transmitter | IC- | LIT-2271 | LIT-2271 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
43 | BL-1P-2-A | TIT-2271 | Temperature Indicator Transmitter | IC- | TIT-2271 | TIT-2271 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
44 | BL-1P-2-A | FIT-2271 | Flow Indicator Transmitter | IC- | FIT-2271 | FIT-2271 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
45 | BL-1P-2-A | PIT-2271 | Pressure Indicator Transmitter | IC- | PIT-2271 | PIT-2271 | JBD-A-2105 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
46 | BL-12P-1-A | JBD-A-2105 | Junction Box | MC- | JBD-A-2105 | JBD-A-2105 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 250 | M40
47 | BL-1P-2-A | PIT-2121A | Pressure Indicator Transmitter | IC- | PIT-2121A | PIT-2121A | JBD-A-2106 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
48 | BL-1P-2-A | PCV-2123A | Pressure Control Valve | IC- | PCV-2123A | PCV-2123A | JBD-A-2106 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
49 | BL-1P-2-A | PDIT-2121A | Diff. Pressure Indicator Transmitter | IC- | PDIT-2121A | PDIT-2121A | JBD-A-2106 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
50 | BL-1P-2-A | LIT-2121A | Level Indicator Transmitter | IC- | LIT-2121A | LIT-2121A | JBD-A-2106 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
51 | BL-1P-2-A | TIT-2121A | Temperature Indicator Transmitter | IC- | TIT-2121A | TIT-2121A | JBD-A-2106 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
52 | BL-1P-2-A | PDIT-2131A | Diff. Pressure Indicator Transmitter | IC- | PDIT-2131A | PDIT-2131A | JBD-A-2106 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
53 | BL-1P-2-A | LIT-2131A | Level Indicator Transmitter | IC- | LIT-2131A | LIT-2131A | JBD-A-2106 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
54 | BL-1P-2-A | TIT-2131A | Temperature Indicator Transmitter | IC- | TIT-2131A | TIT-2131A | JBD-A-2106 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
55 | BL-12P-1-A | JBD-A-2106 | Junction Box | MC- | JBD-A-2106 | JBD-A-2106 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 300 | M40
56 | BL-1P-2-A | PIT-2121B | Pressure Indicator Transmitter | IC- | PIT-2121B | PIT-2121B | JBD-A-2107 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
57 | BL-1P-2-A | PCV-2123B | Pressure Control Valve | IC- | PCV-2123B | PCV-2123B | JBD-A-2107 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
58 | BL-1P-2-A | PDIT-2121B | Diff. Pressure Indicator Transmitter | IC- | PDIT-2121B | PDIT-2121B | JBD-A-2107 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
59 | BL-1P-2-A | LIT-2121B | Level Indicator Transmitter | IC- | LIT-2121B | LIT-2121B | JBD-A-2107 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
60 | BL-1P-2-A | TIT-2121B | Temperature Indicator Transmitter | IC- | TIT-2121B | TIT-2121B | JBD-A-2107 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
61 | BL-1P-2-A | PDIT-2131B | Diff. Pressure Indicator Transmitter | IC- | PDIT-2131B | PDIT-2131B | JBD-A-2107 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
62 | BL-1P-2-A | LIT-2131B | Level Indicator Transmitter | IC- | LIT-2131B | LIT-2131B | JBD-A-2107 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
63 | BL-1P-2-A | TIT-2131B | Temperature Indicator Transmitter | IC- | TIT-2131B | TIT-2131B | JBD-A-2107 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
64 | BL-12P-1-A | JBD-A-2107 | Junction Box | MC- | JBD-A-2107 | JBD-A-2107 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 320 | M40
65 | BL-1P-2-A | PIT-2121C | Pressure Indicator Transmitter | IC- | PIT-2121C | PIT-2121C | JBD-A-2108 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
66 | BL-1P-2-A | PCV-2123C | Pressure Control Valve | IC- | PCV-2123C | PCV-2123C | JBD-A-2108 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
67 | BL-1P-2-A | PDIT-2121C | Diff. Pressure Indicator Transmitter | IC- | PDIT-2121C | PDIT-2121C | JBD-A-2108 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
68 | BL-1P-2-A | LIT-2121C | Level Indicator Transmitter | IC- | LIT-2121C | LIT-2121C | JBD-A-2108 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
69 | BL-1P-2-A | TIT-2121C | Temperature Indicator Transmitter | IC- | TIT-2121C | TIT-2121C | JBD-A-2108 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
70 | BL-1P-2-A | PDIT-2131C | Diff. Pressure Indicator Transmitter | IC- | PDIT-2131C | PDIT-2131C | JBD-A-2108 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
71 | BL-1P-2-A | LIT-2131C | Level Indicator Transmitter | IC- | LIT-2131C | LIT-2131C | JBD-A-2108 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
72 | BL-1P-2-A | TIT-2131C | Temperature Indicator Transmitter | IC- | TIT-2131C | TIT-2131C | JBD-A-2108 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
73 | BL-12P-1-A | JBD-A-2108 | Junction Box | MC- | JBD-A-2108 | JBD-A-2108 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 350 | M40
74 | BL-1P-2-A | TIT-2126A | Temperature Indicator Transmitter | IC- | TIT-2126A | TIT-2126A | JBD-A-2109 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
75 | BL-1P-2-A | HV-2121A | Fan Blade Direction (Temperature Control) | IC- | HV-2121A | HV-2121A | JBD-A-2109 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
76 | BL-1P-2-A | HV-2122A | Fan Blade Direction (Temperature Control) | IC- | HV-2122A | HV-2122A | JBD-A-2109 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
77 | BL-1P-2-A | TIT-2135A | Temperature Indicator Transmitter | IC- | TIT-2135A | TIT-2135A | JBD-A-2109 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
78 | BL-1P-2-A | TCV-2121A | Fan Blade Direction (Temperature Control) | IC- | TCV-2121A | TCV-2121A | JBD-A-1009 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
79 | BL-1P-2-A | TCV-2122A | Fan Blade Direction (Temperature Control) | IC- | TCV-2122A | TCV-2122A | JBD-A-1009 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
80 | BL-1P-2-A | HV-2131A | Fan Blade Direction (Temperature Control) | IC- | HV-2121A | HV-2121A | JBD-A-2109 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
81 | BL-1P-2-A | HV-2132A | Fan Blade Direction (Temperature Control) | IC- | HV-2122A | HV-2122A | JBD-A-2109 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
82 | BL-1P-2-A | TCV-2131A | Fan Blade Direction (Temperature Control) | IC- | TCV-2131A | TCV-2131A | JBD-A-1009 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
83 | BL-1P-2-A | TCV-2132A | Fan Blade Direction (Temperature Control) | IC- | TCV-2132A | TCV-2132A | JBD-A-1009 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
84 | BL-1P-2-A | PIT-2135A | Pressure Indicator Transmitter | IC- | PIT-2135A | PIT-2135A | JBD-A-2109 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | Modified
85 | BL-1P-2-A | PCV-2135A | Pressure Control Valve | IC- | PCV-2135A | PCV-2135A | JBD-A-2109 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | Modified
86 | BL-12P-1-A | JBD-A-2109 | Junction Box | MC- | JBD-A-2109 | JBD-A-2109 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 340 | M40
87 | BL-1P-2-A | TIT-2126B | Temperature Indicator Transmitter | IC- | TIT-2126B | TIT-2126B | JBD-A-2110 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
88 | BL-1P-2-A | HV-2121B | Fan Blade Direction (Temperature Control) | IC- | HV-2121B | HV-2121B | JBD-A-2110 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
89 | BL-1P-2-A | HV-2122B | Fan Blade Direction (Temperature Control) | IC- | HV-2122B | HV-2122B | JBD-A-2110 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
90 | BL-1P-2-A | TIT-2135B | Temperature Indicator Transmitter | IC- | TIT-2135B | TIT-2135B | JBD-A-2110 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
91 | BL-1P-2-A | TCV-2121B | Fan Blade Direction (Temperature Control) | IC- | TCV-2121B | TCV-2121B | JBD-A-1010 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
92 | BL-1P-2-A | TCV-2122B | Fan Blade Direction (Temperature Control) | IC- | TCV-2122B | TCV-2122B | JBD-A-1010 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
93 | BL-1P-2-A | HV-2131B | Fan Blade Direction (Temperature Control) | IC- | HV-2131B | HV-2131B | JBD-A-2110 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
94 | BL-1P-2-A | HV-2132B | Fan Blade Direction (Temperature Control) | IC- | HV-2132B | HV-2132B | JBD-A-2110 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
95 | BL-1P-2-A | TCV-2131B | Fan Blade Direction (Temperature Control) | IC- | TCV-2131B | TCV-2131B | JBD-A-1010 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
96 | BL-1P-2-A | TCV-2132B | Fan Blade Direction (Temperature Control) | IC- | TCV-2132B | TCV-2132B | JBD-A-1010 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
97 | BL-1P-2-A | PIT-2135B | Pressure Indicator Transmitter | IC- | PIT-2135B | PIT-2135B | JBD-A-2110 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | Modified
98 | BL-1P-2-A | PCV-2135B | Pressure Control Valve | IC- | PCV-2135B | PCV-2135B | JBD-A-2110 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | Modified
99 | BL-12P-1-A | JBD-A-2110 | Junction Box | MC- | JBD-A-2110 | JBD-A-2110 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 380 | M40
100 | BL-1P-2-A | TIT-2126C | Temperature Indicator Transmitter | IC- | TIT-2126C | TIT-2126C | JBD-A-2111 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
101 | BL-1P-2-A | HV-2121C | Fan Blade Direction (Temperature Control) | IC- | HV-2121C | HV-2121C | JBD-A-2111 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
102 | BL-1P-2-A | HV-2122C | Fan Blade Direction (Temperature Control) | IC- | HV-2122C | HV-2122C | JBD-A-2111 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
103 | BL-1P-2-A | TIT-2135C | Temperature Indicator Transmitter | IC- | TIT-2135C | TIT-2135C | JBD-A-2111 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
104 | BL-1P-2-A | TCV-2121C | Fan Blade Direction (Temperature Control) | IC- | TCV-2121C | TCV-2121C | JBD-A-1011 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
105 | BL-1P-2-A | TCV-2122C | Fan Blade Direction (Temperature Control) | IC- | TCV-2122C | TCV-2122C | JBD-A-1011 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
106 | BL-1P-2-A | HV-2131C | Fan Blade Direction (Temperature Control) | IC- | HV-2131C | HV-2131C | JBD-A-2111 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
107 | BL-1P-2-A | HV-2132C | Fan Blade Direction (Temperature Control) | IC- | HV-2132C | HV-2132C | JBD-A-2111 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
108 | BL-1P-2-A | TCV-2131C | Fan Blade Direction (Temperature Control) | IC- | TCV-2131C | TCV-2131C | JBD-A-1011 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
109 | BL-1P-2-A | TCV-2132C | Fan Blade Direction (Temperature Control) | IC- | TCV-2132C | TCV-2132C | JBD-A-1011 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
110 | BL-1P-2-A | PIT-2135C | Pressure Indicator Transmitter | IC- | PIT-2135C | PIT-2135C | JBD-A-2111 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | Modified
111 | BL-1P-2-A | PCV-2135C | Pressure Control Valve | IC- | PCV-2135C | PCV-2135C | JBD-A-2111 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | Modified
112 | BL-12P-1-A | JBD-A-2111 | Junction Box | MC- | JBD-A-2111 | JBD-A-2111 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 420 | M40
113 | BL-1P-2-A | PDIT-2141 | Diff. Pressure Indicator Transmitter | IC- | PDIT-2141 | PDIT-2141 | JBD-A-2112 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
114 | BL-1P-2-A | LIT-2141 | Level Indicator Transmitter | IC- | LIT-2141 | LIT-2141 | JBD-A-2112 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
115 | BL-1P-2-A | PDIT-2143 | Diff. Pressure Indicator Transmitter | IC- | PDIT-2143 | PDIT-2143 | JBD-A-2112 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
116 | BL-1P-2-A | PIT-2151 | Pressure Indicator Transmitter | IC- | PIT-2151 | PIT-2151 | JBD-A-2112 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
117 | BL-1P-2-A | PCV-2151 | Pressure Control Vavle | IC- | PCV-2151 | PCV-2151 | JBD-A-2112 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
118 | BL-1P-2-A | PCV-2152 | Pressure Control Vavle | IC- | PCV-2152 | PCV-2152 | JBD-A-2112 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
119 | BL-1P-2-A | LIT-2162 | Level Indicator Transmitter | IC- | LIT-2162 | LIT-2162 | JBD-A-2112 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
120 | BL-12P-1-A | JBD-A-2112 | Junction Box | MC- | JBD-A-2112 | JBD-A-2112 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 370 | M40
121 | BL-1P-2-A | LIT-2221 | Level Indicator Transmitter | IC- | LIT-2221 | LIT-2221 | JBD-A-2113 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
122 | BL-1P-2-A | LIT-2223A | Level Indicator Transmitter | IC- | LIT-2223A | LIT-2223A | JBD-A-2113 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
123 | BL-1P-2-A | LIT-2223B | Level Indicator Transmitter | IC- | LIT-2223B | LIT-2223B | JBD-A-2113 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
124 | BL-1P-2-A | LIT-2251 | Level Indicator Transmitter | IC- | LIT-2251 | LIT-2251 | JBD-A-2113 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
125 | BL-1P-2-A | LIT-2273 | Level Indicator Transmitter | IC- | LIT-2273 | LIT-2273 | JBD-A-2113 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
126 | BL-1P-2-A | LIT-2293 | Level Indicator Transmitter | IC- | LIT-2293 | LIT-2293 | JBD-A-2113 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
127 | BL-12P-1-A | JBD-A-2113 | Junction Box | MC- | JBD-A-2113 | JBD-A-2113 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 500 | M40
128 | BL-1P-2-A | PDI-2201 | Dif. Pressure Indicator Transmitter | IC- | PDI-2201 | PDI-2201 | JBD-A-2114 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
129 | BL-1P-2-A | PDI-2202 | Dif. Pressure Indicator Transmitter | IC- | PDI-2202 | PDI-2202 | JBD-A-2114 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
130 | BL-1P-2-A | AIA-2201 | Humidity Analyzer | IC- | AIA-2201 | AIA-2201 | JBD-A-2114 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
131 | BL-1P-2-A | PIT-2201 | Pressure Indicator Transmitter | IC- | PIT-2201 | PIT-2201 | JBD-A-2114 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
132 | BL-1P-2-A | PCV-2201 | Pressure Control Valve | IC- | PCV-2201 | PCV-2201 | JBD-A-2114 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
133 | BL-1P-2-A | PIT-2203 | Pressure Indicator Transmitter | IC- | PIT-2203 | PIT-2203 | JBD-A-2114 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
134 | BL-1P-2-A | PIT-2203-AO | Pressure Indicator Transmitter | IC- | PIT-2203-AO | PIT-2203-AO | JBD-A-1014 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
135 | BL-1P-2-A | FIT-2201 | Flow Indicator Transmitter | IC- | FIT-2201 | FIT-2201 | JBD-A-1014 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
136 | BL-12P-1-A | JBD-A-2114 | Junction Box | MC- | JBD-A-2114 | JBD-A-2114 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 400 | M40
137 | BL-1P-2-A | AIT-2212 | C02 Analyzer | IC- | AIT-2212 | AIT-2212 | JBD-A-2115 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | Modified
138 | BL-1P-2-A | AIT-2213 | H20 Analyzer | IC- | AIT-2213 | AIT-2213 | JBD-A-2115 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | Modified
139 | BL-1P-2-A | PDIA-2211 | Dif. Pressure Indicator Transmitter | IC- | PDIA-2211 | PDIA-2211 | JBD-A-2115 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
140 | BL-1P-2-A | PDIA-2212 | Dif. Pressure Indicator Transmitter | IC- | PDIA-2212 | PDIA-2212 | JBD-A-2115 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
141 | BL-1P-2-A | PIT-2213 | Pressure Indicator Transmitter | IC- | PIT-2213 | PIT-2213 | JBD-A-2115 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
142 | BL-1P-2-A | PCV-2211 | Pressure Control Valve | IC- | PCV-2211 | PCV-2211 | JBD-A-2115 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
143 | BL-1P-2-A | FIT-2211 | Flow Indicator Transmitter | IC- | FIT-2211 | FIT-2211 | JBD-A-2115 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
144 | BL-1P-2-A | TT-2211 | Temperature Transmitter | IC- | TT-2211 | TT-2211 | JBD-A-2115 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
145 | BL-1P-2-A | PIT-2214 | Pressure Indicator Transmitter | IC- | PIT-2214 | PIT-2214 | JBD-A-2115 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20 | ADDED
146 | BL-12P-1-A | JBD-A-2115 | Junction Box | MC- | JBD-A-2115 | JBD-A-2115 | DCS | FRT | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 400 | M40
147 | BL-1P-2-A | FIT-2241 | Flow Indicator Transmitter | IC- | FIT-2241 | FIT-2241 | JBD-A-1015 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
148 | BL-1P-2-A | FIT-2242 | Flow Indicator Transmitter | IC- | FIT-2242 | FIT-2242 | JBD-A-1015 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
149 | BL-1P-2-A | FIT-2243 | Flow Indicator Transmitter | IC- | FIT-2243 | FIT-2243 | JBD-A-1015 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
150 | BL-1P-2-A | FIT-2244 | Flow Indicator Transmitter | IC- | FIT-2244 | FIT-2244 | JBD-A-1015 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
151 | BL-1P-2-A | FIT-2245 | Flow Indicator Transmitter | IC- | FIT-2245 | FIT-2245 | JBD-A-1015 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V |  | M20 | Deleted
152 | BL-1P-2-A | TI-2261A | Temperature Indicator | IC- | TI-2261A | TI-2261A | LCP-IG-2201 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
153 | BL-1P-2-A | TI-2261B | Temperature Indicator | IC- | TI-2261B | TI-2261B | LCP-IG-2201 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
154 | BL-1P-2-A | TI-2261C | Temperature Indicator | IC- | TI-2261C | TI-2261C | LCP-IG-2201 | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 15 | M20
155 | BL-7P-1-A | LCP-IG-2201 | LOCAL CONTROL PANEL | MC- | LCP-IG-2201 | LCP-IG-2201 | DCS | FRT | SWA | IS | 7 | PAIR | 1 | Individual & Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 420 | M32
156 | BL-1P-2-A | LIT-2281 | Level Indicator Transmitter | IC- | LIT-2281 | LIT-2281 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 250 | M20 | DIRECT
157 | BL-1P-2-A | LIT-2291 | Level Indicator Transmitter | IC- | LIT-2291 | LIT-2291 | DCS | FRT | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue | NOTE 3 | 300/500 V | 200 | M20 | DIRECT
158 | GY-1P-2-A | EZSO-2111 | Limit Switch Open | IC- | EZSO-2111 | EZSO-2111 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
159 | GY-1P-2-A | EZSC-2111 | Limit Switch Close | IC- | EZSC-2111 | EZSC-2111 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
160 | GY-1P-2-A | EZSO-2113 | Limit Switch Open | IC- | EZSO-2113 | EZSO-2113 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
161 | GY-1P-2-A | EZSC-2113 | Limit Switch Close | IC- | EZSC-2113 | EZSC-2113 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
162 | GY-1P-2-A | XZSO-2110 | Limit Switch Open | IC- | XZSO-2110 | XZSO-2110 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
163 | GY-1P-2-A | XZSC-2110 | Limit Switch Close | IC- | XZSC-2110 | XZSC-2110 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
164 | GY-1P-2-A | EZSC-2272 | Limit Switch Close | IC- | EZSC-2272 | EZSC-2272 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
165 | GY-1P-2-A | EZSO-2272 | Limit Switch Open | IC- | EZSO-2272 | EZSO-2272 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
166 | GY-1P-2-A | XZSC-2271 | Limit Switch Close | IC- | XZSC-2271 | XZSC-2271 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
167 | GY-1P-2-A | XZSO-2271 | Limit Switch Open | IC- | XZSO-2271 | XZSO-2271 | JBD-D-2101 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
168 | GY-12P-1-A | JBD-D-2101 | Junction Box | MC- | JBD-D-2101 | JBD-D-2101 | DCS | FRT | SWA | NIS | 12 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 250 | M40
169 | GY-1P-2-A | XZSC-2122A | Limit Switch Close | IC- | XZSC-2122A | XZSC-2122A | JBD-D-2102 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
170 | GY-1P-2-A | XZSO-2122A | Limit Switch Open | IC- | XZSO-2122A | XZSO-2122A | JBD-D-2102 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
171 | GY-1P-2-A | XZSC-2131A | Limit Switch Close | IC- | XZSC-2131A | XZSC-2131A | JBD-D-2102 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
172 | GY-1P-2-A | XZSO-2131A | Limit Switch Open | IC- | XZSO-2131A | XZSO-2131A | JBD-D-2102 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
173 | GY-7P-1-A | JBD-D-2102 | Junction Box | MC- | JBD-D-2102 | JBD-D-2102 | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 300 | M32
174 | GY-1P-2-A | XZSC-2122B | Limit Switch Close | IC- | XZSC-2122B | XZSC-2122B | JBD-D-2103 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
175 | GY-1P-2-A | XZSO-2122B | Limit Switch Open | IC- | XZSO-2122B | XZSO-2122B | JBD-D-2103 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
176 | GY-1P-2-A | XZSC-2131B | Limit Switch Close | IC- | XZSC-2131B | XZSC-2131B | JBD-D-2103 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
177 | GY-1P-2-A | XZSO-2131B | Limit Switch Open | IC- | XZSO-2131B | XZSO-2131B | JBD-D-2103 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
178 | GY-7P-1-A | JBD-D-2103 | Junction Box | MC- | JBD-D-2103 | JBD-D-2103 | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 320 | M32
179 | GY-1P-2-A | XZSC-2122C | Limit Switch Close | IC- | XZSC-2122C | XZSC-2122C | JBD-D-2104 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
180 | GY-1P-2-A | XZSO-2122C | Limit Switch Open | IC- | XZSO-2122C | XZSO-2122C | JBD-D-2104 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
181 | GY-1P-2-A | XZSC-2131C | Limit Switch Close | IC- | XZSC-2131C | XZSC-2131C | JBD-D-2104 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
182 | GY-1P-2-A | XZSO-2131C | Limit Switch Open | IC- | XZSO-2131C | XZSO-2131C | JBD-D-2104 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
183 | GY-7P-1-A | JBD-D-2104 | Junction Box | MC- | JBD-D-2104 | JBD-D-2104 | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 350 | M32
184 | GY-1P-2-A | XZSC-2144 | Limit Switch Close | IC- | XZSC-2141 | XZSC-2141 | JBD-D-2105 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20 | Modified
185 | GY-1P-2-A | XZSO-2144 | Limit Switch Open | IC- | XZSO-2141 | XZSO-2141 | JBD-D-2105 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20 | Modified
186 | GY-1P-2-A | BZSC-2141 | Limit Switch Close | IC- | BZSC-2141 | BZSC-2141 | JBD-D-2105 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
187 | GY-1P-2-A | BZSO-2141 | Limit Switch Open | IC- | BZSO-2141 | BZSO-2141 | JBD-D-2105 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
188 | GY-1P-2-A | BZSC-2151 | Limit Switch Close | IC- | BZSC-2151 | BZSC-2151 | JBD-D-2105 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
189 | GY-1P-2-A | BZSO-2151 | Limit Switch Open | IC- | BZSO-2151 | BZSO-2151 | JBD-D-2105 | FRT | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray | NOTE 3 | 300/500 V | 15 | M20
190 | GY-12P-1-A | JBD-D-2105 | Junction Box | MC- | JBD-D-2104 | JBD-D-2105 | DCS | FRT | SWA | NIS | 12 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 370 | M40
191 | GY-1P-3-A | PSOV-2110 | Solenoid Valve | IC- | PSOV-2110 | PSOV-2110 | JBD-S-2101 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20 | ADDED
192 | GY-1P-3-A | PSOV-2122A | Solenoid Valve | IC- | PSOV-2122A | PSOV-2122A | JBD-S-2101 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20
193 | GY-1P-3-A | PSOV-2131A | Solenoid Valve | IC- | PSOV-2131A | PSOV-2131A | JBD-S-2101 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20
194 | GY-1P-3-A | PSOV-2271 | Solenoid Valve | IC- | PSOV-2271 | PSOV-2271 | JBD-S-2101 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20
195 | GY-7P-3-A | JBD-S-2101 | Junction Box | MC- | JBD-S-2101 | JBD-S-2101 | DCS | FRT | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 300 | M32
196 | GY-1P-3-A | PSOV-2122B | Solenoid Valve | IC- | PSOV-2122B | PSOV-2122B | JBD-S-2102 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20
197 | GY-1P-3-A | PSOV-2131B | Solenoid Valve | IC- | PSOV-2131B | PSOV-2131B | JBD-S-2102 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20
198 | GY-7P-3-A | JBD-S-2102 | Junction Box | MC- | JBD-S-2102 | JBD-S-2102 | DCS | FRT | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 320 | M32
199 | GY-1P-3-A | PSOV-2122C | Solenoid Valve | IC- | PSOV-2122C | PSOV-2122C | JBD-S-2103 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20
200 | GY-1P-3-A | PSOV-2131C | Solenoid Valve | IC- | PSOV-2131C | PSOV-2131C | JBD-S-2103 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20
201 | GY-7P-3-A | JBD-S-2103 | Junction Box | MC- | JBD-S-2103 | JBD-S-2103 | DCS | FRT | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 350 | M32
202 | GY-1P-3-A | PSOV-2144 | Solenoid Valve | IC- | PSOV-2141 | PSOV-2141 | JBD-S-2104 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20 | Modified
203 | GY-1P-3-A | PSOV-2142 | Solenoid Valve | IC- | PSOV-2142 | PSOV-2142 | JBD-S-2104 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20
204 | GY-1P-3-A | PSOV-2143 | Solenoid Valve | IC- | PSOV-2143 | PSOV-2143 | JBD-S-2104 | FRT | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 15 | M20
205 | GY-7P-3-A | JBD-S-2104 | Junction Box | MC- | JBD-S-2104 | JBD-S-2104 | DCS | FRT | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray | NOTE 3 | 600/1000 V | 370 | M32
206 | GY-12P-1-A | XSP-2201A | STOP Command | MC- | LCP-C-2203A | LCP-C-2203A | DCS | FRT | SWA | NIS | 12 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 400 | M40
207 |  | XSS-2201A | START Command
208 |  | XR-2201A | Running Status
209 |  | XF-2201A | Fault Status
210 |  | XA-2201A | Availibility
211 |  | XD-2201A | Duty/Standby Status
212 |  | TAH-2201A | Temperature High Alarm
213 |  | PAL-2201A | Pressure Low Alarm
214 |  | PAH-2201A | Pressure Low Alarm
215 |  | HSD-2201A | Duty/Standby Command
216 | GY-12P-1-A | XSP-2201B | STOP Command | MC- | LCP-C-2203B | LCP-C-2203B | DCS | FRT | SWA | NIS | 12 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 400 | M40
217 |  | XSS-2201B | START Command
218 |  | XR-2201B | Running Status
219 |  | XF-2201B | Fault Status
220 |  | XA-2201B | Availibility
221 |  | XD-2201B | Duty/Standby Status
222 |  | TAH-2201B | Temperature High Alarm
223 |  | PAL-2201B | Pressure Low Alarm
224 |  | PAH-2201B | Pressure High Alarm
225 |  | HSD-2201B | Duty/Standby Command
226 | GY-7P-1-A | XR-2201 | Running Status | MC- | LCP-DR-2203 | LCP-DR-2203 | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 400 | M32
227 |  | XF-2201 | Command Fault Alarm
228 | GY-12P-1-A | XSP-2211 | STOP Command | MC- | LCP-G-2204 | LCP-G-2204 | DCS | FRT | SWA | NIS | 12 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 380 | M40
229 |  | XSS-2211 | START Command
230 |  | XR-2211 | Running Status
231 |  | XF-2211 | Fault Status
232 |  | XA-2211 | Availibility
233 |  | TAH-2211 | Temperature High Alarm
234 |  | PAL-2211 | Pressure Low Alarm
235 |  | PAH-2211 | Pressure High Alarm
236 |  | XR-2212 | Running Status
237 |  | XF-2212 | Fault Status
238 | GY-12P-1-A | XF-2231 | FAULT STATUS | MC- | LCP-PK-2207 | LCP-PK-2207 | DCS | FRT | SWA | NIS | 12 | PAIR | 1 | Overall Screen | gray | NOTE 3 | 300/500 V | 270 | M40 | Deleted
239 |  | XSP-2231 | STOP Command | [16 empty] | ADDED
240 |  | LALL-PK-2231A | Level Low Low Alarm | [16 empty] | Deleted
241 |  | XR-2231A | Running Status | [16 empty] | Modified
242 |  | XR-2231B | Running Status | [16 empty] | Modified
243 |  | XR-2231C | Running Status | [16 empty] | ADDED
244 |  | XR-2231D | Running Status | [7 empty] | 7 | PAIR |  |  | Gray | NOTE 3 |  |  |  | ADDED
245 |  | XR-2231F | Running Status | [16 empty] | ADDED
246 |  | XF-2231A | FAULT STATUS | [16 empty] | Modified
247 |  | XF-2231B | FAULT STATUS | [16 empty] | Modified
248 |  | XF-2231C | FAULT STATUS | [16 empty] | ADDED
249 |  | XF-2231D | FAULT STATUS | [16 empty] | ADDED
250 |  | XF-2231F | FAULT STATUS | [16 empty] | ADDED
251 | GY-12P-1-A | XR-2261 | LPG Bottle Inservuce | MC- | LCP-IG-2201 | LCP-IG-2201 | DCS | FRT | SWA | NIS | 12 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 420 | M40
252 |  | XR-2261A | Pilot 1 Status
253 |  | XR-2261B | Pilot 2 Status
254 |  | XR-2261C | Pilot 3 Status
255 |  | XA-2261 | Common Fault Alarm
256 |  | XF-2261 | Auto Ignition Failure
257 |  | XA-2262 | Burn Back Alarm
258 | GY-7P-1-A | XF-2241A | Fault Alarm | MC- | LCP-PK-2208 | LCP-PK-2208 | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 270 | M40
259 |  | XR-2241A | Running Status
260 |  | XF-2241B | Fault Alarm
261 |  | XR-2241B | Running Status
262 |  | LALL-2241 | Level Low Low Alarm
263 | GY-7P-1 | XSS-2124A | Start Permission | MC- | UCP-A | UCP-A | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M32 | Modified
264 |  | XSS-2123A | START Command | [16 empty] | Modified
265 |  | XSP-2123A | STOP Command | [16 empty] | Modified
266 | GY-7P-1 | XSS-2124B | Start Permission | MC- | UCP-B | UCP-B | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M32 | Modified
267 |  | XSS-2123B | START Command | [16 empty] | Modified
268 |  | XSP-2123B | STOP Command | [16 empty] | Modified
269 | GY-7P-1 | XSS-2124C | Start Permission | MC- | UCP-C | UCP-C | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M32 | Modified
270 |  | XSS-2123C | START Command | [16 empty] | Modified
271 |  | XSP-2123C | STOP Command | [16 empty] | Modified
272 | GY-7P-1-A | HSL-2102A | HAND SWITCH LOCAL/REMOTE | MC- | MOV-2102A | MOV-2102A | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 300 | M32 | ADDED
273 |  | XF-2102A | FAULT FEEDBACK | [16 empty] | ADDED
274 |  | MZTO-2102A | LIMIT SWITCH OPEN | [16 empty] | ADDED
275 |  | MZTC-2102A | LIMIT SWITCH CLOSE | [16 empty] | ADDED
276 |  | HSCIO-2102A | HAND SWITCH OPEN | [16 empty] | ADDED
277 |  | HSCIO-2102A | HAND SWITCH CLOSE | [16 empty] | ADDED
278 | GY-7P-1-A | HSL-2102B | HAND SWITCH LOCAL/REMOTE | MC- | MOV-2102B | MOV-2102B | DCS | FRT | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 300 | M32 | ADDED
279 |  | XF-2102B | FAULT FEEDBACK | [16 empty] | ADDED
280 |  | MZTO-2102B | LIMIT SWITCH OPEN | [16 empty] | ADDED
281 |  | MZTC-2102B | LIMIT SWITCH CLOSE | [16 empty] | ADDED
282 |  | HSCIO-2102B | HAND SWITCH OPEN | [16 empty] | ADDED
283 |  | HSCIO-2102B | HAND SWITCH CLOSE | [16 empty] | ADDED
284 | GY-20P-1-A | XL-2111A | Local Remote Status | MC- | IRP-DCS 1 | IRP | DCS | FRT | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M50
285 |  | XR-2111A | Running Status
286 |  | XF-2111A | Fault Status
287 |  | XL-2111B | Local Remote Status
288 |  | XR-2111B | Running Status
289 |  | XF-2111B | Fault Status
290 |  | XF-2121A | FAULT STATUS
291 |  | XR-2121A | Running Status
292 |  | XL-2121A | Local / Remote Status
293 |  | XF-2122A | FAULT STATUS
294 |  | XR-2122A | Running Status
295 |  | XL-2122A | Local / Remote Status
296 |  | XF-2121B | FAULT STATUS
297 |  | XR-2121B | Running Status
298 |  | XL-2121B | Local / Remote Status
299 |  | XF-2122B | FAULT STATUS
300 | GY-20P-1-A | XR-2122B | Running Status | MC- | IRP-DCS 2 | IRP | DCS | FRT | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M50
301 |  | XL-2122B | Local / Remote Status
302 |  | XF-2121C | FAULT STATUS
303 |  | XR-2121C | Running Status
304 |  | XL-2121C | Local / Remote Status
305 |  | XF-2122C | FAULT STATUS
306 |  | XR-2122C | Running Status
307 |  | XL-2122C | Local / Remote Status
308 |  | XF-2131A | FAULT STATUS
309 |  | XR-2131A | Running Status
310 |  | XL-2131A | Local / Remote Status
311 |  | XF-2132A | FAULT STATUS
312 |  | XR-2132A | Running Status
313 |  | XL-2132A | Local / Remote Status
314 |  | XF-2131B | FAULT STATUS
315 |  | XR-2131B | Running Status
316 | GY-20P-1-A | XL-2131B | Local / Remote Status | MC- | IRP-DCS 3 | IRP | DCS | FRT | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M50
317 |  | XF-2132B | FAULT STATUS
318 |  | XR-2132B | Running Status
319 |  | XL-2132B | Local / Remote Status
320 |  | XF-2131C | FAULT STATUS
321 |  | XR-2131C | Running Status
322 |  | XL-2131C | Local / Remote Status
323 |  | XF-2132C | FAULT STATUS
324 |  | XR-2132C | Running Status
325 |  | XL-2132C | Local / Remote Status
326 |  | XF-2161A | FAULT STATUS
327 |  | XR-2161A | Running Status
328 |  | XL-2161A | Local / Remote Status
329 |  | XF-2161B | FAULT STATUS
330 |  | XR-2161B | Running Status
331 |  | XL-2161B | Local / Remote Status
332 | GY-20P-1-A | XF-2221A | FAULT STATUS | MC- | IRP-DCS 4 | IRP | DCS | FRT | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M50
333 |  | XR-2221A | Running Status
334 |  | XL-2221A | Local / Remote Status
335 |  | XF-2221B | FAULT STATUS
336 |  | XR-2221B | Running Status
337 |  | XL-2221B | Local / Remote Status
338 |  | XF-2222A | FAULT STATUS
339 |  | XR-2222A | Running Status
340 |  | XL-2222A | Local / Remote Status
341 |  | XF-2222B | FAULT STATUS
342 |  | XR-2222B | Running Status
343 |  | XL-2222B | Local / Remote Status
344 |  | XF-2251A | FAULT STATUS
345 |  | XR-2251A | Running Status
346 |  | XL-2251A | Local / Remote Status
347 |  | XF-2251B | FAULT STATUS
348 | GY-20P-1-A | XR-2251B | Running Status | MC- | IRP-DCS 5 | IRP | DCS | FRT | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M50
349 |  | XL-2251B | Local / Remote Status
350 |  | XF-2281 | FAULT STATUS
351 |  | XR-2281 | Running Status
352 |  | XF-2291 | FAULT STATUS
353 |  | XR-2291 | Running Status | [16 empty] | ADDED
354 |  | XL-2291 | Local / Remote Status
355 |  | XF-2293 | FAULT STATUS | [16 empty] | ADDED
356 |  | XR-2293 | Running Status | [16 empty] | ADDED
357 |  | XL-2293 | Local / Remote Status | [16 empty] | ADDED
358 | GY-20P-1-A | XSS-2111A | START Command | MC- | IRP-DCS 6 | IRP | DCS | FRT | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M50
359 |  | XSP-2111A | STOP Command
360 |  | XSS-2111B | START Command
361 |  | XSP-2111B | STOP Command
362 |  | XSP-2121A | STOP Command
363 |  | XSS-2121A | START Command
364 |  | XSP-2122A | STOP Command
365 |  | XSS-2122A | START Command
366 |  | XSP-2121B | STOP Command
367 |  | XSS-2121B | START Command
368 |  | XSP-2122B | STOP Command
369 |  | XSS-2122B | START Command
370 |  | XSP-2121C | STOP Command
371 |  | XSS-2121C | START Command
372 |  | XSP-2122C | STOP Command
373 |  | XSS-2122C | START Command
374 | GY-20P-1-A | XSP-2131A | STOP Command | MC- | IRP-DCS 7 | IRP | DCS | FRT | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M50
375 |  | XSS-2131A | START Command
376 |  | XSP-2132A | STOP Command
377 |  | XSS-2132A | START Command
378 |  | XSP-2131B | STOP Command
379 |  | XSS-2131B | START Command
380 |  | XSP-2132B | STOP Command
381 |  | XSS-2132B | START Command
382 |  | XSP-2131C | STOP Command
383 |  | XSS-2131C | START Command
384 |  | XSP-2132C | STOP Command
385 |  | XSS-2132C | START Command
386 |  | XSP-2161A | STOP Command
387 |  | XSS-2161A | START Command
388 |  | XSP-2161B | STOP Command
389 |  | XSS-2161B | START Command
390 | GY-20P-1-A | XSP-2221A | STOP Command | MC- | IRP-DCS 8 | IRP | DCS | FRT | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M50
391 |  | XSS-2221A | START Command
392 |  | XSP-2221B | STOP Command
393 |  | XSS-2221B | START Command
394 |  | XSP-2222A | STOP Command
395 |  | XSS-2222A | START Command
396 |  | XSP-2222B | STOP Command
397 |  | XSS-2222B | START Command
398 | GY-20P-1-A | XSP-2251A | STOP Command | MC- | IRP-DCS 9 | IRP | DCS | FRT | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M50
399 |  | XSS-2251A | START Command
400 |  | XSP-2251B | STOP Command
401 |  | XSS-2251B | START Command
402 |  | HSP-2291 | STOP Command
403 |  | HSS-2291 | START Command | [16 empty] | ADDED
404 |  | HSP-2293 | STOP Command | [16 empty] | ADDED
405 |  | HSS-2293 | START Command | [16 empty] | ADDED
406 |  | XSS-2104 | START Command | [16 empty] | Deleted
407 |  | XSP-2104 | STOP Command | [16 empty] | Deleted
408 | GY-7P-1 | ESDR 0-UPS | UPS FAILURE | MC- | DCS-ESD | DCS | ESD | FRT | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M32 | ADDED
409 |  | ESDR 1-PCS | PCS FAILURE | [16 empty] | ADDED
410 |  | ESDR 1-FLR | FLARE IGNITION FAILURE | [16 empty] | ADDED
411 | GY-7P-1 | CI-UPS1 | CURRENT MEASURMENT UPS1 | MC- | DCS-UPS1 | DCS | UPS1 | FRT | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M32 | ADDED
412 |  | VI-UPS1 | VOLTAGE MEASURMENT UPS1 | [16 empty] | ADDED
413 |  | XF-UPS1 | UPS1 FAILURE | [16 empty] | ADDED
414 | GY-7P-1 | CI-UPS2 | CURRENT MEASURMENT UPS2 | MC- | DCS-UPS2 | DCS | UPS2 | FRT | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray | NOTE 3 | 300/500 V | 50 | M32 | ADDED
415 |  | VI-UPS2 | VOLTAGE MEASURMENT UPS2 | [16 empty] | ADDED
416 |  | XF-UPS2 | UPS2 FAILURE | [16 empty] | ADDED
417 | BR-1P-2-FA | PIT-2111 | Pressure Indicator Transmitter | IC- | PIT-2111 | PIT-2111 | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
418 | BR-1P-2-FA | LIT-2112 | Level Indicator Transmitter | IC- | LIT-2111 | LIT-2111 | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | Modified
419 | BR-1P-2-FA | LIT-2115 | Level Indicator Transmitter | IC- | LIT-2115 | LIT-2115 | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
420 | BR-1P-2-FA | PIT-2115 | Pressure Indicator Transmitter | IC- | PIT-2115 | PIT-2115 | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
421 | BR-1P-2-FA | PIT-2113A | Pressure Indicator Transmitter | IC- | PIT-2113A | PIT-2113A | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
422 | BR-1P-2-FA | PIT-2113B | Pressure Indicator Transmitter | IC- | PIT-2113B | PIT-2113B | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
423 | BR-1P-2-FA | LIT-2117 | Level Indicator Transmitter | IC- | LIT-2117 | LIT-2117 | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
424 | BR-1P-2-FA | LIT-2118 | Level Indicator Transmitter | IC- | LIT-2118 | LIT-2118 | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
425 | BR-1P-2-FA | PIT-2116 | Pressure Indicator Transmitter | IC- | PIT-2116 | PIT-2116 | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
426 | BR-1P-2-FA | LIT-2272 | Level Indicator Transmitter | IC- | LIT-2272 | LIT-2272 | JBE-A-2101 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
427 | BR-12P-1-FA | JBE-A-2101 | Junction Box | MC- | JBE-A-2101 | JBE-A-2101 | ESD | FRS | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 250 | M40
428 | BR-1P-2-FA | LIT-2122A | Level Indicator Transmitter | IC- | LIT-2122A | LIT-2122A | JBE-A-2102 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
429 | BR-1P-2-FA | PIT-2122A | Pressure Indicator Transmitter | IC- | PIT-2122A | PIT-2122A | JBE-A-2102 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
430 | BR-1P-2-FA | PIT-2125A | Pressure Indicator Transmitter | IC- | PIT-2125A | PIT-2125A | JBE-A-2102 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
431 | BR-1P-2-FA | TIT-2124A | Temperature Indicator Transmitter | IC- | TIT-2124A | TIT-2124A | JBE-A-2102 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
432 | BR-1P-2-FA | LIT-2132A | Level Indicator Transmitter | IC- | LIT-2132A | LIT-2132A | JBE-A-2102 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
433 | BR-1P-2-FA | PIT-2131A | Pressure Indicator Transmitter | IC- | PIT-2131A | PIT-2131A | JBE-A-2102 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
434 | BR-1P-2-FA | PIT-2134A | Pressure Indicator Transmitter | IC- | PIT-2134A | PIT-2134A | JBE-A-2102 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
435 | BR-1P-2-FA | TIT-2134A | Temperature Indicator Transmitter | IC- | TIT-2134A | TIT-2134A | JBE-A-2102 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
436 | BR-12P-1-FA | JBE-A-2102 | Junction Box | MC- | JBE-A-2102 | JBE-A-2102 | ESD | FRS | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 300 | M40
437 | BR-1P-2-FA | LIT-2122B | Level Indicator Transmitter | IC- | LIT-2122B | LIT-2122B | JBE-A-2103 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
438 | BR-1P-2-FA | PIT-2122B | Pressure Indicator Transmitter | IC- | PIT-2122B | PIT-2122B | JBE-A-2103 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
439 | BR-1P-2-FA | PIT-2125B | Pressure Indicator Transmitter | IC- | PIT-2125B | PIT-2125B | JBE-A-2103 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
440 | BR-1P-2-FA | TIT-2124B | Temperature Indicator Transmitter | IC- | TIT-2124B | TIT-2124B | JBE-A-2103 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
441 | BR-1P-2-FA | LIT-2132B | Level Indicator Transmitter | IC- | LIT-2132B | LIT-2132B | JBE-A-2103 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
442 | BR-1P-2-FA | PIT-2131B | Pressure Indicator Transmitter | IC- | PIT-2131B | PIT-2131B | JBE-A-2103 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
443 | BR-1P-2-FA | PIT-2134B | Pressure Indicator Transmitter | IC- | PIT-2134B | PIT-2134B | JBE-A-2103 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
444 | BR-1P-2-FA | TIT-2134B | Temperature Indicator Transmitter | IC- | TIT-2134B | TIT-2134B | JBE-A-2103 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
445 | BR-12P-1-FA | JBE-A-2103 | Junction Box | MC- | JBE-A-2103 | JBE-A-2103 | ESD | FRS | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 320 | M40
446 | BR-1P-2-FA | LIT-2122C | Level Indicator Transmitter | IC- | LIT-2122C | LIT-2122C | JBE-A-2104 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
447 | BR-1P-2-FA | PIT-2122C | Pressure Indicator Transmitter | IC- | PIT-2122C | PIT-2122C | JBE-A-2104 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
448 | BR-1P-2-FA | PIT-2125C | Pressure Indicator Transmitter | IC- | PIT-2125C | PIT-2125C | JBE-A-2104 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
449 | BR-1P-2-FA | TIT-2124C | Temperature Indicator Transmitter | IC- | TIT-2124C | TIT-2124C | JBE-A-2104 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
450 | BR-1P-2-FA | LIT-2132C | Level Indicator Transmitter | IC- | LIT-2132C | LIT-2132C | JBE-A-2104 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
451 | BR-1P-2-FA | PIT-2131C | Pressure Indicator Transmitter | IC- | PIT-2131C | PIT-2131C | JBE-A-2104 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
452 | BR-1P-2-FA | PIT-2134C | Pressure Indicator Transmitter | IC- | PIT-2134C | PIT-2134C | JBE-A-2104 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
453 | BR-1P-2-FA | TIT-2134C | Temperature Indicator Transmitter | IC- | TIT-2134C | TIT-2134C | JBE-A-2104 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
454 | BR-12P-1-FA | JBE-A-2104 | Junction Box | MC- | JBE-A-2104 | JBE-A-2104 | ESD | FRS | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 350 | M40
455 | BR-1P-2-FA | TIT-2125A | Temperature Indicator Transmitter | IC- | TIT-2125A | TIT-2125A | JBE-A-2105 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
456 | BR-1P-2-FA | TIT-2136A | Temperature Indicator Transmitter | IC- | TIT-2136A | TIT-2136A | JBE-A-2105 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
457 | BR-7P-1-FA | JBE-A-2105 | Junction Box | MC- | JBE-A-2105 | JBE-A-2105 | ESD | FRS | SWA | IS | 7 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 340 | M32
458 | BR-1P-2-FA | TIT-2125B | Temperature Indicator Transmitter | IC- | TIT-2125B | TIT-2125B | JBE-A-2106 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
459 | BR-1P-2-FA | TIT-2136B | Temperature Indicator Transmitter | IC- | TIT-2136B | TIT-2136B | JBE-A-2106 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
460 | BR-7P-1-FA | JBE-A-2106 | Junction Box | MC- | JBE-A-2106 | JBE-A-2106 | ESD | FRS | SWA | IS | 7 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 380 | M32
461 | BR-1P-2-FA | TIT-2125C | Temperature Indicator Transmitter | IC- | TIT-2125C | TIT-2125C | JBE-A-2107 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
462 | BR-1P-2-FA | TIT-2136C | Temperature Indicator Transmitter | IC- | TIT-2136C | TIT-2136C | JBE-A-2107 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
463 | BR-7P-1-FA | JBE-A-2107 | Junction Box | MC- | JBE-A-2107 | JBE-A-2107 | ESD | FRS | SWA | IS | 7 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 420 | M32
464 | BR-1P-2-FA | LIT-2142 | Level Indicator Transmitter | IC- | LIT-2142 | LIT-2142 | JBE-A-2108 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
465 | BR-1P-2-FA | LIT-2161 | Level Indicator Transmitter | IC- | LIT-2161 | LIT-2161 | JBE-A-2108 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
466 | BR-7P-1-FA | JBE-A-2108 | Junction Box | MC- | JBE-A-2108 | JBE-A-2108 | ESD | FRS | SWA | IS | 7 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 370 | M32
467 | BR-1P-2-FA | LIT-2222 | Level Indicator Transmitter | IC- | LIT-2222 | LIT-2222 | JBE-A-2109 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
468 | BR-1P-2-FA | LIT-2252A | Level Indicator Transmitter | IC- | LIT-2252A | LIT-2252A | JBE-A-2109 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
469 | BR-1P-2-FA | LIT-2252B | Level Indicator Transmitter | IC- | LIT-2252B | LIT-2252B | JBE-A-2109 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
470 | BR-1P-2-FA | LIT-2252C | Level Indicator Transmitter | IC- | LIT-2252C | LIT-2252C | JBE-A-2109 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
471 | BR-1P-2-FA | LIT-2253 | Level Indicator Transmitter | IC- | LIT-2253 | LIT-2253 | JBE-A-2109 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20
472 | BR-12P-1-FA | JBE-A-2109 | Junction Box | MC- | JBE-A-2109 | JBE-A-2109 | ESD | FRS | SWA | IS | 7 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 500 | M32
473 | BR-1P-2-FA | PIT-2201A | Pressure Switch Low Low | IC- | PIT-2201A | PIT-2201A | JBE-A-2110 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | ADDED
474 | BR-1P-2-FA | PIT-2201B | Pressure Switch Low Low | IC- | PIT-2201B | PIT-2201B | JBE-A-2110 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | ADDED
475 | BR-1P-2-FA | PIT-2201C | Pressure Switch Low Low | IC- | PIT-2201C | PIT-2201C | JBE-A-2110 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | ADDED
476 | BR-1P-2-FA | PIT-2211A | Pressure Switch Low Low | IC- | PIT-2211A | PIT-2211A | JBE-A-2110 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | ADDED
477 | BR-1P-2-FA | PIT-2211B | Pressure Switch Low Low | IC- | PIT-2211B | PIT-2211B | JBE-A-2110 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | ADDED
478 | BR-1P-2-FA | PIT-2211C | Pressure Switch Low Low | IC- | PIT-2211C | PIT-2211C | JBE-A-2110 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | ADDED
479 | BR-12P-1-FA | JBE-A-2110 | Junction Box | MC- | JBE-A-2110 | JBE-A-2110 | ESD | FRS | SWA | IS | 12 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 400 | M40
480 | BR-1P-2-FA | PIT-3201A | Pressure Switch Low Low | IC- | PIT-3201A | PIT-3201A | JBE-A-2111 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | ADDED
481 | BR-1P-2-FA | PIT-3201B | Pressure Switch Low Low | IC- | PIT-3201B | PIT-3201B | JBE-A-2111 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | ADDED
482 | BR-1P-2-FA | PIT-3201C | Pressure Switch Low Low | IC- | PIT-3201C | PIT-3201C | JBE-A-2111 | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | ADDED
483 | BR-7P-1-FA | JBE-A-2111 | Junction Box | MC- | JBE-A-2111 | JBE-A-2111 | ESD | FRS | SWA | IS | 7 | PAIR | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 300 | M32
484 | GR-1P-2-FA | EZSC-2101 | Limit Switch Close | IC- | EZSC-2101 | EZSC-2101 | JBE-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
485 | GR-1P-2-FA | EZSO-2101 | Limit Switch Open | IC- | EZSO-2101 | EZSO-2101 | JBE-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
486 | GR-1P-2-FA | EZSC-2102 | Limit Switch Close | IC- | EZSC-2102 | EZSC-2102 | JBE-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
487 | GR-1P-2-FA | EZSO-2102 | Limit Switch Open | IC- | EZSO-2102 | EZSO-2102 | JBE-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
488 | GR-1P-2-FA | EZSC-2112 | Limit Switch Close | IC- | EZSC-2112 | EZSC-2112 | JBE-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
489 | GR-1P-2-FA | EZSO-2112 | Limit Switch Open | IC- | EZSO-2112 | EZSO-2112 | JBE-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
490 | GR-7P-1-FA | JBE-D-2101 | Junction Box | MC- | JBE-D-2101 | JBE-D-2101 | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 300 | M40
491 | GR-1P-2-FA | VSHH-2121A | Vibration Switch | IC- | VSHH-2121A | VSHH-2121A | JBE-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
492 | GR-1P-2-FA | VSHH-2122A | Vibration Switch | IC- | VSHH-2122A | VSHH-2122A | JBE-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
493 | GR-1P-2-FA | VSHH-2131A | Vibration Switch | IC- | VSHH-2131A | VSHH-2131A | JBE-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
494 | GR-1P-2-FA | VSHH-2132A | Vibration Switch | IC- | VSHH-2132A | VSHH-2132A | JBE-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
495 | GR-7P-1-FA | JBE-D-2102 | Junction Box | MC- | JBE-D-2102 | JBE-D-2102 | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 340 | M32
496 | GR-1P-2-FA | VSHH-2121B | Vibration Switch | IC- | VSHH-2121B | VSHH-2121B | JBE-D-2103 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
497 | GR-1P-2-FA | VSHH-2122B | Vibration Switch | IC- | VSHH-2122B | VSHH-2122B | JBE-D-2103 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
498 | GR-1P-2-FA | VSHH-2131B | Vibration Switch | IC- | VSHH-2131B | VSHH-2131B | JBE-D-2103 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
499 | GR-1P-2-FA | VSHH-2132B | Vibration Switch | IC- | VSHH-2132B | VSHH-2132B | JBE-D-2103 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
500 | GR-7P-1-FA | JBE-D-2103 | Junction Box | MC- | JBE-D-2103 | JBE-D-2103 | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 380 | M32
501 | GR-1P-2-FA | VSHH-2121C | Vibration Switch | IC- | VSHH-2121C | VSHH-2121C | JBE-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
502 | GR-1P-2-FA | VSHH-2122C | Vibration Switch | IC- | VSHH-2122C | VSHH-2122C | JBE-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
503 | GR-1P-2-FA | VSHH-2131C | Vibration Switch | IC- | VSHH-2131C | VSHH-2131C | JBE-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
504 | GR-1P-2-FA | VSHH-2132C | Vibration Switch | IC- | VSHH-2132C | VSHH-2132C | JBE-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
505 | GR-7P-1-FA | JBE-D-2104 | Junction Box | MC- | JBE-D-2104 | JBE-D-2104 | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 420 | M32
506 | GR-1P-2-FA | XZSC-2142 | Limit Switch Close | IC- | XZSC-2142 | XZSC-2142 | JBE-D-2105 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
507 | GR-1P-2-FA | XZSO-2142 | Limit Switch Open | IC- | XZSO-2142 | XZSO-2142 | JBE-D-2105 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
508 | GR-1P-2-FA | XZSC-2143 | Limit Switch Close | IC- | XZSC-2143 | XZSC-2143 | JBE-D-2105 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
509 | GR-1P-2-FA | XZSO-2143 | Limit Switch Open | IC- | XZSO-2143 | XZSO-2143 | JBE-D-2105 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20
510 | GR-7P-1-FA | JBE-D-2105 | Junction Box | MC- | JBE-D-2105 | JBE-D-2105 | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 370 | M32
511 | GR-1P-2-FA | EZSC-2231 | Limit Switch Close | IC- | EZSC-2131 | EZSC-2131 | JBE-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
512 | GR-1P-2-FA | EZSO-2231 | Limit Switch Open | IC- | EZSO-2131 | EZSO-2131 | JBE-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
513 | GR-1P-2-FA | PSLL-2201A | Pressure Switch Low Low | IC- | PSLL-2201A | PSLL-2201A | JBE-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M20 | DELETED
514 | GR-1P-2-FA | PSLL-2201B | Pressure Switch Low Low | IC- | PSLL-2201B | PSLL-2201B | JBE-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M20 | DELETED
515 | GR-1P-2-FA | PSLL-2201C | Pressure Switch Low Low | IC- | PSLL-2201C | PSLL-2201C | JBE-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M20 | DELETED
516 | GR-1P-2-FA | PSLL-2211A | Pressure Switch Low Low | IC- | PSLL-2211A | PSLL-2211A | JBE-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M20 | DELETED
517 | GR-1P-2-FA | PSLL-2211B | Pressure Switch Low Low | IC- | PSLL-2211B | PSLL-2211B | JBE-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M20 | DELETED
518 | GR-1P-2-FA | PSLL-2211C | Pressure Switch Low Low | IC- | PSLL-2211C | PSLL-2211C | JBE-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | - | M20 | DELETED
519 | GR-7P-1-FA | JBE-D-2106 | Junction Box | MC- | JBE-D-2106 | JBE-D-2106 | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 400 | M32
520 | GR-1P-3-FA | ESOV-2101 | Solenoid Valve | IC- | ESOV-2101 | ESOV-2101 | JBE-S-2101 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
521 | GR-1P-3-FA | ESOV-2102 | Solenoid Valve | IC- | ESOV-2102 | ESOV-2102 | JBE-S-2101 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
522 | GR-1P-3-FA | ESOV-2112 | Solenoid Valve | IC- | ESOV-2112 | ESOV-2112 | JBE-S-2101 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
523 | GR-7P-3-FA | JBE-S-2101 | Junction Box | MC- | JBE-S-2101 | JBE-S-2101 | ESD | FRS | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 300 | M25
524 | GR-1P-3-FA | ESOV-2111 | Solenoid Valve | IC- | ESOV-2111 | ESOV-2111 | JBE-S-2102 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
525 | GR-1P-3-FA | ESOV-2113 | Solenoid Valve | IC- | ESOV-2113 | ESOV-2113 | JBE-S-2102 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
526 | GR-1P-3-FA | ESOV-2272 | Solenoid Valve | IC- | ESOV-2272 | ESOV-2272 | JBE-S-2102 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
527 | GR-1P-3-FA | ESOV-2271 | Solenoid Valve | IC- | ESOV-2271 | ESOV-2271 | JBE-S-2102 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
528 | GR-7P-3-FA | JBE-S-2102 | Junction Box | MC- | JBE-S-2102 | JBE-S-2102 | ESD | FRS | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 250 | M32
529 | GR-1P-3-FA | ESOV-2121A | Solenoid Valve | IC- | ESOV-2121A | ESOV-2121A | JBE-S-2103 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
530 | GR-1P-3-FA | ESOV-2122A | Solenoid Valve | IC- | ESOV-2122A | ESOV-2122A | JBE-S-2103 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
531 | GR-1P-3-FA | ESOV-2131A | Solenoid Valve | IC- | ESOV-2131A | ESOV-2131A | JBE-S-2103 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
532 | GR-1P-3-FA | BSOV-2131A | Solenoid Valve | IC- | ESOV-2131A | BSOV-2131A | JBE-S-2103 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20 | ADDED
533 | GR-7P-3-FA | JBE-S-2103 | Junction Box | MC- | JBE-S-2103 | JBE-S-2103 | ESD | FRS | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 300 | M32
534 | GR-1P-3-FA | ESOV-2121B | Solenoid Valve | IC- | ESOV-2121B | ESOV-2121B | JBE-S-2104 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
535 | GR-1P-3-FA | ESOV-2122B | Solenoid Valve | IC- | ESOV-2122B | ESOV-2122B | JBE-S-2104 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
536 | GR-1P-3-FA | ESOV-2131B | Solenoid Valve | IC- | ESOV-2131B | ESOV-2131B | JBE-S-2104 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
537 | GR-1P-3-FA | BSOV-2131B | Solenoid Valve | IC- | ESOV-2131A | BSOV-2131B | JBE-S-2104 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20 | ADDED
538 | GR-7P-3-FA | JBE-S-2104 | Junction Box | MC- | JBE-S-2104 | JBE-S-2104 | ESD | FRS | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 320 | M32
539 | GR-1P-3-FA | ESOV-2121C | Solenoid Valve | IC- | ESOV-2121C | ESOV-2121C | JBE-S-2105 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
540 | GR-1P-3-FA | ESOV-2122C | Solenoid Valve | IC- | ESOV-2122C | ESOV-2122C | JBE-S-2105 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
541 | GR-1P-3-FA | ESOV-2131C | Solenoid Valve | IC- | ESOV-2131C | ESOV-2131C | JBE-S-2105 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
542 | GR-1P-3-FA | BSOV-2131C | Solenoid Valve | IC- | BSOV-2131C | ESOV-2131C | JBE-S-2105 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20 | ADDED
543 | GR-7P-3-FA | JBE-S-2105 | Junction Box | MC- | JBE-S-2105 | JBE-S-2105 | ESD | FRS | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 350 | M32
544 | GR-1P-3-FA | BSOV-2132A | Solenoid Valve | IC- | BSOV-2132A | BSOV-2132A | JBE-S-2106 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
545 | GR-1P-3-FA | ESOV-2133A | Solenoid Valve | IC- | ESOV-2133A | ESOV-2133A | JBE-S-2106 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
546 | GR-7P-3-FA | JBE-S-2106 | Junction Box | MC- | JBE-S-2106 | JBE-S-2106 | ESD | FRS | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 340 | M32
547 | GR-1P-3-FA | BSOV-2132B | Solenoid Valve | IC- | BSOV-2132B | BSOV-2132B | JBE-S-2107 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
548 | GR-1P-3-FA | ESOV-2133B | Solenoid Valve | IC- | ESOV-2133B | ESOV-2133B | JBE-S-2107 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
549 | GR-7P-3-FA | JBE-S-2107 | Junction Box | MC- | JBE-S-2107 | JBE-S-2107 | ESD | FRS | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 380 | M32
550 | GR-1P-3-FA | BSOV-2132C | Solenoid Valve | IC- | BSOV-2132C | BSOV-2132C | JBE-S-2108 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
551 | GR-1P-3-FA | ESOV-2133C | Solenoid Valve | IC- | ESOV-2133C | ESOV-2133C | JBE-S-2108 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
552 | GR-7P-3-FA | JBE-S-2108 | Junction Box | MC- | JBE-S-2108 | JBE-S-2108 | ESD | FRS | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 420 | M32
553 | RD-1P-3-FA | ESOV-2141 | Solenoid Valve | IC- | ESOV-2141 | ESOV-2141 | JBE-S-1009 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Red | NOTE 3 | 600/1000 V |  | M20 | DELETED
554 | GR-1P-3-FA | BSOV-2141 | Solenoid Valve | IC- | BSOV-2141 | BSOV-2141 | JBE-S-2109 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
555 | GR-1P-3-FA | ESOV-2142 | Solenoid Valve | IC- | ESOV-2142 | ESOV-2142 | JBE-S-2109 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
556 | GR-1P-3-FA | ESOV-2143 | Solenoid Valve | IC- | ESOV-2143 | ESOV-2143 | JBE-S-2109 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
557 | GR-1P-3-FA | ESOV-2144 | Solenoid Valve | IC- | ESOV-2144 | ESOV-2143 | JBE-S-2109 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20 | ADDED
558 | GR-1P-3-FA | BSOV-2151 | Solenoid Valve | IC- | BSOV-2151 | BSOV-2151 | JBE-S-2109 | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 15 | M20
559 | GR-7P-3-FA | JBE-S-2109 | Junction Box | MC- | JBE-S-2109 | JBE-S-2109 | ESD | FRS | SWA | NIS | 7 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 370 | M32
560 | GR-7P-1-F | ESDR2A-C-2101-A | Trip Command With Depressurizing | MC- | UCP-A | UCP-A | ESD | FRS | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32 | MODIFIED
561 |  | ESDR2-C-2101-A | Trip Command Without Depressurizing | [16 empty] | MODIFIED
562 |  | ESD2A-C-2101-A | Trip Alarm With Depressurizing | [16 empty] | MODIFIED
563 |  | ESD2-C-2101-A | Trip Alarm Without Depressurizing | [16 empty] | MODIFIED
564 | GR-7P-1-F | ESDR2A-C-2101-B | Trip Command With Depressurizing | MC- | UCP-B | UCP-B | ESD | FRS | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32 | MODIFIED
565 |  | ESDR2-C-2101-B | Trip Command Without Depressurizing | [16 empty] | MODIFIED
566 |  | ESD2A-C-2101-B | Trip Alarm With Depressurizing | [16 empty] | MODIFIED
567 |  | ESD2-C-2101-B | Trip Alarm Without Depressurizing | [16 empty] | MODIFIED
568 | GR-7P-1-F | ESDR2A-C-2101-C | Trip Command With Depressurizing | MC- | UCP-C | UCP-C | ESD | FRS | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32 | MODIFIED
569 |  | ESDR2-C-2101-C | Trip Command Without Depressurizing | [16 empty] | MODIFIED
570 |  | ESD2A-C-2101-C | Trip Alarm With Depressurizing | [16 empty] | MODIFIED
571 |  | ESD2-C-2101-C | Trip Alarm Without Depressurizing | [16 empty] | MODIFIED
572 | GR-7P-1-FA | ESD-PK-2208 | Trip Command | MC- | LCP-2208 | LCP-2208 | ESD | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 300 | M32 | ADDED
573 |  | LALL-2241 | Level Alarm Low Low | [16 empty] | ADDED
574 | GR-20P-1-FA | ESD-P-2111-A | Trip Command-P-2101-A | MC- | IRP-ESD 1 | IRP | ESD | FRS | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M50 | MODIFIED
575 |  | ESD-P-2111-B | Trip Command-P-2101-B | [16 empty] | MODIFIED
576 |  | ESD-AE-2101-A-1 | Trip Command-AE-2101-A | [16 empty] | MODIFIED
577 |  | ESD-AE-2101-A-2 | Trip Command-AE-2101-A | [16 empty] | MODIFIED
578 |  | ESD-AE-2101-B-1 | Trip Command-AE-2101-B | [16 empty] | MODIFIED
579 |  | ESD-AE-2101-B-2 | Trip Command-AE-2101-B | [16 empty] | MODIFIED
580 |  | ESD-AE-2101-C-1 | Trip Command-AE-2101-C | [16 empty] | MODIFIED
581 |  | ESD-AE-2101-C-2 | Trip Command-AE-2101-C | [16 empty] | MODIFIED
582 |  | ESD-AE-2102-A-1 | Trip Command-AE-2102-A | [16 empty] | MODIFIED
583 |  | ESD-AE-2102-A-2 | Trip Command-AE-2102-A | [16 empty] | MODIFIED
584 |  | ESD-AE-2102-B-1 | Trip Command-AE-2102-B | [16 empty] | MODIFIED
585 |  | ESD-AE-2102-B-2 | Trip Command-AE-2102-B | [16 empty] | MODIFIED
586 |  | ESD-AE-2102-C-1 | Trip Command-AE-2102-C | [16 empty] | MODIFIED
587 |  | ESD-AE-2102-C-2 | Trip Command-AE-2102-C | [16 empty] | MODIFIED
588 |  | ESD-P-2161-A | Trip Command-P-2103-A | [16 empty] | MODIFIED
589 |  | ESD-P-2161-B | Trip Command-P-2103-B | [16 empty] | MODIFIED
590 | GR-20P-1-FA | ESD-P-2202-A | Trip Command-P-2202-A | MC- | IRP-ESD 2 | IRP | ESD | FRS | SWA | NIS | 20 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M50 | MODIFIED
591 |  | ESD-P-2202-B | Trip Command-P-2202-B | [16 empty] | MODIFIED
592 |  | ESD-P-2203-A | Trip Command-P-2203-A | [16 empty] | MODIFIED
593 |  | ESD-P-2203-B | Trip Command-P-2203-B | [16 empty] | MODIFIED
594 |  | ESD-2201A | Trip Command-P-2201-A | [16 empty] | MODIFIED
595 |  | ESD-2201B | Trip Command-P-2201-B | [16 empty] | MODIFIED
596 |  | TR-2293 | Trip Command-P-2104 | [16 empty] | DELETED
597 |  | ESD 0-EL1 | EMERGENCY + NORMAL POWER ISOLATION | [16 empty] | ADDED
598 |  | ESD 1A-EL1 | POWER ISOLATION IN PROCESS AREA | [16 empty] | ADDED
599 |  | ESDR 1-EL1 | NETWORK POWER FAILURE SWITCH ACTIVATION | [16 empty] | ADDED
600 |  | ESD-P-2206 | - | [16 empty] | MODIFIED
601 | GR-7P-1-F | ESDR 0-UPS | UPS FAILURE | MC- | DCS-ESD | ESD | DCS | FRS | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32 | ADDED
602 |  | ESDR 1-PCS | PCS FAILURE | [16 empty] | ADDED
603 |  | ESDR 1-FLR | FLARE IGNITION FAILURE | [16 empty] | ADDED
604 | GR-7P-1-F | ESDR 0-FGS | CONFIRMED FLAMMABLE GAS IN HVAC INTAKE (COMMAND FROM FGS) | MC- | FGS-ESD | ESD | DCS | FRS | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32 | ADDED
605 |  | ESDR 1A-FGS | CONFIRMED FLAMMABLE GAS IN PROCESS AREA (COMMAND FROM FGS) | [16 empty] | ADDED
606 |  | ESD 2A-FGS-A | CONFIRMED FIRE IN FIRE ZONE AREA (COMMAND FROM FGS)- TRAIN A | [16 empty] | ADDED
607 | GR-7P-1-F | ESD 0-EL2 | UPS BATTERY ISOLATION | MC- | UPS-ESD | ESD | UPS CHARGER | FRS | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32 | ADDED
608 |  | ESDR 1-DC | DC CHARGER FAILURE | [16 empty] | ADDED
609 | GR-20P-1-F | ESD0-LAMP | TOTAL PLANT SHUT DOWN WITH AUTOMATIC DEPRESSURIZING (ESD0) | MC- | CONSOLE-ESD 1 | ESD | ED CONSOLE | FRS | - | NIS | 20 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M50 | ADDED
610 |  | ESD1A-LAMP | PROCESS EMERGENCY SHUT DOWN WITH DEPRESSURIZING (ESD1A) | [16 empty] | ADDED
611 |  | ESD2A-A-LAMP | TRAIN A SHUT DOWN WITH DEPRESSURIZING | [16 empty] | ADDED
612 |  | ESD2A-B-LAMP | TRAIN B SHUT DOWN WITH DEPRESSURIZING | [16 empty] | ADDED
613 |  | ESD2A-C-LAMP | TRAIN C SHUT DOWN WITH DEPRESSURIZING | [16 empty] | ADDED
614 |  | LAMP-ESD-INH | ESD INHIBIT LAMP | [16 empty] | ADDED
615 |  | LAMP-ESD-RST | ESD RESET LAMP | [16 empty] | ADDED
616 |  | ESD1-LAMP | PROCESS EMERGENCY SHUT DOWN WITHOUT DEPRESSURIZING (ESD1) | [16 empty] | ADDED
617 |  | ESD2-A-LAMP | TRAIN A SHUT DOWN WITHOUT DEPRESSURIZING | [16 empty] | ADDED
618 |  | ESD2-B-LAMP | TRAIN B SHUT DOWN WITHOUT DEPRESSURIZING | [16 empty] | ADDED
619 |  | ESD2-C-LAMP | TRAIN C SHUT DOWN WITHOUT DEPRESSURIZING | [16 empty] | ADDED
620 |  | ESD0-PB | TOTAL PLANT SHUT DOWN WITH AUTOMATIC DEPRESSURIZING (ESD0) P.B. | [16 empty] | ADDED
621 |  | ESD1A-PB | PROCESS EMERGENCY SHUT DOWN WITH DEPRESSURIZING (ESD1A) P.B. | [16 empty] | ADDED
622 |  | ESD2A-A-PB | TRAIN A SHUT DOWN WITH DEPRESSURIZING (ESD2A-A) P.B. | [16 empty] | ADDED
623 |  | ESD2A-B-PB | TRAIN B SHUT DOWN WITH DEPRESSURIZING (ESD2A-B) P.B. | [16 empty] | ADDED
624 |  | ESD2A-C-PB | TRAIN C SHUT DOWN WITH DEPRESSURIZING (ESD2A-C) P.B. | [16 empty] | ADDED
625 | GR-20P-1-F | ESD-INH | ESD INHIBIT SELECTOR SWITCH | MC- | CONSOLE-ESD 2 | ESD | ESD CONSOLE | FRS | - | NIS | 20 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M50 | ADDED
626 |  | ESD-RST | RESET P.B. | [16 empty] | ADDED
627 |  | ESD1-PB | PROCESS EMERGENCY SHUT DOWN WITHOUT DEPRESSURIZING (ESD1) P.B. | [16 empty] | ADDED
628 |  | ESD2-A-PB | TRAIN A SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-A) P.B. | [16 empty] | ADDED
629 |  | ESD2-B-PB | TRAIN B SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-B) P.B. | [16 empty] | ADDED
630 |  | ESD2-C-PB | TRAIN C SHUT DOWN WITHOUT DEPRESSURIZING (ESD2A-C) P.B. | [16 empty] | ADDED
631 |  | ESDI 0-EX | EXISTING SYSTEM ESD 0 status | [16 empty] | ADDED
632 |  | ESDI 1-EX | EXISTING SYSTEM ESD 1 status | [16 empty] | ADDED
633 |  | ESDI 1A-EX | EXISTING SYSTEM ESD 1A status | [16 empty] | ADDED
634 | GR-7P-1-F | ESDI 0- NEW | NEW SYSTEM ESD 0 status | MC- | NSYSTEM | ESD | NEW SYSTEM | FRS | - | NIS | 7 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M32 | ADDED
635 |  | ESDI 1- NEW | NEW SYSTEM ESD 1 status | [16 empty] | ADDED
636 |  | ESDI 1A- NEW | NEW SYSTEM ESD 1A status | [16 empty] | ADDED
637 | GR-1P-3-FA | ESOV-2231 | Solenoid Valve | IC- | ESOV-2131 | ESOV-2131 | ESD | FRS | SWA | NIS | 1 | PAIR | 2.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 600/1000 V | 340 | M20 | Direct
638 | BR-1P-2-FA | PIT-2202 | Pressure Indicator Transmitter | IC- | PIT-2202 | PIT-2202 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 400 | M20 | Direct
639 | BR-1P-2-FA | PIT-2281 | Pressure Indicator Transmitter | IC- | PIT-2281 | PIT-2281 | ESD | FRS | SWA | IS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 250 | M20 | Direct
640 | BR-1P-2-FA | ESD-PK-2207 | SHOUTDOWN | IC- | ESD-PK-2207 | ESD-PK-2207 | ESD | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 300 | M20 | Direct
641 | RD-1T-2-FA | FGD-1001 | Flammable Gas Detector | IC- | FGD-1001 | FGD-1001 | JBF-A-2101 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
642 | RD-1T-2-FA | FGD-1002 | Flammable Gas Detector | IC- | FGD-1002 | FGD-1002 | JBF-A-2101 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
643 | RD-1T-2-FA | FGD-1003 | Flammable Gas Detector | IC- | FGD-1003 | FGD-1003 | JBF-A-2101 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
644 | RD-1T-2-FA | TGD-1001 | Toxic Gas Detector | IC- | TGD-1001 | TGD-1001 | JBF-A-2101 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
645 | RD-1T-2-FA | TGD-1002 | Toxic Gas Detector | IC- | TGD-1002 | TGD-1002 | JBF-A-2101 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
646 | RD-1T-2-FA | TGD-1003 | Toxic Gas Detector | IC- | TGD-1003 | TGD-1003 | JBF-A-2101 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
647 | RD-12T-1-FA | JBF-A-2101 | Junction Box | MC- | JBF-A-2102 | JBF-A-2102 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 270 | M32 | MODIFIED
648 | RD-1T-2-FA | FGD-1004 | Flammable Gas Detector | IC- | FGD-1004 | FGD-1004 | JBF-A-2102 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
649 | RD-1T-2-FA | FGD-1005 | Flammable Gas Detector | IC- | FGD-1005 | FGD-1005 | JBF-A-2102 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
650 | RD-1T-2-FA | FGD-1006 | Flammable Gas Detector | IC- | FGD-1006 | FGD-1006 | JBF-A-2102 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
651 | RD-1T-2-FA | FGD-1007 | Flammable Gas Detector | IC- | FGD-1007 | FGD-1007 | JBF-A-1002 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | DELETED
652 | RD-1T-2-FA | TGD-1004 | Toxic Gas Detector | IC- | TGD-1004 | TGD-1004 | JBF-A-1002 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | - | M20 | DELETED
653 | RD-1T-2-FA | TGD-1005 | Toxic Gas Detector | IC- | TGD-1005 | TGD-1005 | JBF-A-2102 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
654 | RD-1T-2-FA | TGD-1006 | Toxic Gas Detector | IC- | TGD-1006 | TGD-1006 | JBF-A-2102 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
655 | RD-1T-2-FA | TGD-1007 | Toxic Gas Detector | IC- | TGD-1007 | TGD-1007 | JBF-A-2102 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
656 | RD-12T-1-FA | JBF-A-2102 | Junction Box | MC- | JBF-A-2102 | JBF-A-2102 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 250 | M40 | MODIFIED
657 | RD-1T-2-FA | FGD-1008 | Flammable Gas Detector | IC- | FGD-1008 | FGD-1008 | JBF-A-2103 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
658 | RD-1T-2-FA | FGD-1009 | Flammable Gas Detector | IC- | FGD-1009 | FGD-1009 | JBF-A-2103 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
659 | RD-1T-2-FA | FGD-1010 | Flammable Gas Detector | IC- | FGD-1010 | FGD-1010 | JBF-A-2103 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
660 | RD-1T-2-FA | TGD-1008 | Toxic Gas Detector | IC- | TGD-1008 | TGD-1008 | JBF-A-2103 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
661 | RD-1T-2-FA | TGD-1009 | Toxic Gas Detector | IC- | TGD-1009 | TGD-1009 | JBF-A-2103 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
662 | RD-1T-2-FA | TGD-1010 | Toxic Gas Detector | IC- | TGD-1010 | TGD-1010 | JBF-A-2103 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
663 | RD-12T-1-FA | JBF-A-2103 | Junction Box | MC- | JBF-A-2103 | JBF-A-2103 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 270 | M40 | MODIFIED
664 | RD-1T-2-FA | FD-2001A | Flame Detector | IC- | FD-2001A | FD-2001A | JBF-A-2104 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
665 | RD-1T-2-FA | FD-2002A | Flame Detector | IC- | FD-2002A | FD-2002A | JBF-A-2104 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
666 | RD-1T-2-FA | FGD-2001A | Flammable Gas Detector | IC- | FGD-2001A | FGD-2001A | JBF-A-2104 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
667 | RD-1T-2-FA | FGD-2002A | Flammable Gas Detector | IC- | FGD-2002A | FGD-2002A | JBF-A-2104 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
668 | RD-1T-2-FA | FGD-2003A | Flammable Gas Detector | IC- | FGD-2003A | FGD-2003A | JBF-A-2104 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
669 | RD-1T-2-FA | TGD-2001A | Toxic Gas Detector | IC- | TGD-2001A | TGD-2001A | JBF-A-2104 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
670 | RD-1T-2-FA | TGD-2002A | Toxic Gas Detector | IC- | TGD-2002A | TGD-2002A | JBF-A-2104 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
671 | RD-1T-2-FA | TGD-2003A | Toxic Gas Detector | IC- | TGD-2003A | TGD-2003A | JBF-A-2104 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
672 | RD-12T-1-FA | JBF-A-2104 | Junction Box | MC- | JBF-A-2104 | JBF-A-2104 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 300 | M40 | MODIFIED
673 | RD-1T-2-FA | FD-2003A | Flame Detector | IC- | FD-2003A | FD-2003A | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
674 | RD-1T-2-FA | FD-2004A | Flame Detector | IC- | FD-2004A | FD-2004A | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
675 | RD-1T-2-FA | FGD-2007A | Flammable Gas Detector | IC- | FGD-2007A | FGD-2007A | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
676 | RD-1T-2-FA | FGD-2008A | Flammable Gas Detector | IC- | FGD-2008A | FGD-2008A | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
677 | RD-1T-2-FA | FGD-2009A | Flammable Gas Detector | IC- | FGD-2009A | FGD-2009A | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
678 | RD-1T-2-FA | TGD-2007A | Toxic Gas Detector | IC- | TGD-2007A | TGD-2007A | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
679 | RD-1T-2-FA | TGD-2008A | Toxic Gas Detector | IC- | TGD-2008A | TGD-2008A | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
680 | RD-1T-2-FA | TGD-2009A | Toxic Gas Detector | IC- | TGD-2009A | TGD-2009A | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
681 | RD-1T-2-FA | FGD-2010 | Flammable Gas Detector | IC- | FGD-2010 | FGD-2010 | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
682 | RD-1T-2-FA | TGD-2010 | Toxic Gas Detector | IC- | TGD-2010 | TGD-2010 | JBF-A-2105 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
683 | RD-12T-1-FA | JBF-A-2105 | Junction Box | MC- | JBF-A-2105 | JBF-A-2105 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 300 | M40 | MODIFIED
684 | RD-1T-2-FA | FGD-2004A | Flammable Gas Detector | IC- | FGD-2004A | FGD-2004A | JBF-A-2106 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
685 | RD-1T-2-FA | FGD-2005A | Flammable Gas Detector | IC- | FGD-2005A | FGD-2005A | JBF-A-2106 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
686 | RD-1T-2-FA | FGD-2006A | Flammable Gas Detector | IC- | FGD-2006A | FGD-2006A | JBF-A-2106 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
687 | RD-1T-2-FA | TGD-2004A | Toxic Gas Detector | IC- | TGD-2004A | TGD-2004A | JBF-A-2106 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
688 | RD-1T-2-FA | TGD-2005A | Toxic Gas Detector | IC- | TGD-2005A | TGD-2005A | JBF-A-2106 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
689 | RD-1T-2-FA | TGD-2006A | Toxic Gas Detector | IC- | TGD-2006A | TGD-2006A | JBF-A-2106 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
690 | RD-12T-1-FA | JBF-A-2106 | Junction Box | MC- | JBF-A-2106 | JBF-A-2106 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 340 | M40 | MODIFIED
691 | RD-1T-2-FA | FD-2001B | Flame Detector | IC- | FD-2001B | FD-2001B | JBF-A-2107 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
692 | RD-1T-2-FA | FD-2002B | Flame Detector | IC- | FD-2002B | FD-2002B | JBF-A-2107 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
693 | RD-1T-2-FA | FGD-2001B | Flammable Gas Detector | IC- | FGD-2001B | FGD-2001B | JBF-A-2107 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
694 | RD-1T-2-FA | FGD-2002B | Flammable Gas Detector | IC- | FGD-2002B | FGD-2002B | JBF-A-2107 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
695 | RD-1T-2-FA | FGD-2003B | Flammable Gas Detector | IC- | FGD-2003B | FGD-2003B | JBF-A-2107 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
696 | RD-1T-2-FA | TGD-2001B | Toxic Gas Detector | IC- | TGD-2001B | TGD-2001B | JBF-A-2107 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
697 | RD-1T-2-FA | TGD-2002B | Toxic Gas Detector | IC- | TGD-2002B | TGD-2002B | JBF-A-2107 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
698 | RD-1T-2-FA | TGD-2003B | Toxic Gas Detector | IC- | TGD-2003B | TGD-2003B | JBF-A-2107 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
699 | RD-12T-1-FA | JBF-A-2107 | Junction Box | MC- | JBF-A-2107 | JBF-A-2107 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 320 | M40 | MODIFIED
700 | RD-1T-2-FA | FD-2003B | Flame Detector | IC- | FD-2003B | FD-2003B | JBF-A-2108 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
701 | RD-1T-2-FA | FD-2004B | Flame Detector | IC- | FD-2004B | FD-2004B | JBF-A-2108 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
702 | RD-1T-2-FA | FGD-2007B | Flammable Gas Detector | IC- | FGD-2007B | FGD-2007B | JBF-A-2108 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
703 | RD-1T-2-FA | FGD-2008B | Flammable Gas Detector | IC- | FGD-2008B | FGD-2008B | JBF-A-2108 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
704 | RD-1T-2-FA | FGD-2009B | Flammable Gas Detector | IC- | FGD-2009B | FGD-2009B | JBF-A-2108 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
705 | RD-1T-2-FA | TGD-2007B | Toxic Gas Detector | IC- | TGD-2007B | TGD-2007B | JBF-A-2108 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
706 | RD-1T-2-FA | TGD-2008B | Toxic Gas Detector | IC- | TGD-2008B | TGD-2008B | JBF-A-2108 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
707 | RD-1T-2-FA | TGD-2009B | Toxic Gas Detector | IC- | TGD-2009B | TGD-2009B | JBF-A-2108 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
708 | RD-12T-1-FA | JBF-A-2108 | Junction Box | MC- | JBF-A-2108 | JBF-A-2108 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 320 | M40 | MODIFIED
709 | RD-1T-2-FA | FGD-2004B | Flammable Gas Detector | IC- | FGD-2004B | FGD-2004B | JBF-A-2109 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
710 | RD-1T-2-FA | FGD-2005B | Flammable Gas Detector | IC- | FGD-2005B | FGD-2005B | JBF-A-2109 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
711 | RD-1T-2-FA | FGD-2006B | Flammable Gas Detector | IC- | FGD-2006B | FGD-2006B | JBF-A-2109 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
712 | RD-1T-2-FA | TGD-2004B | Toxic Gas Detector | IC- | TGD-2004B | TGD-2004B | JBF-A-2109 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
713 | RD-1T-2-FA | TGD-2005B | Toxic Gas Detector | IC- | TGD-2005B | TGD-2005B | JBF-A-2109 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
714 | RD-1T-2-FA | TGD-2006B | Toxic Gas Detector | IC- | TGD-2006B | TGD-2006B | JBF-A-2109 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
715 | RD-12T-1-FA | JBF-A-2109 | Junction Box | MC- | JBF-A-2109 | JBF-A-2109 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 380 | M40 | MODIFIED
716 | RD-1T-2-FA | FD-2001C | Flame Detector | IC- | FD-2001C | FD-2001C | JBF-A-2110 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
717 | RD-1T-2-FA | FD-2002C | Flame Detector | IC- | FD-2002C | FD-2002C | JBF-A-2110 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
718 | RD-1T-2-FA | FGD-2001C | Flammable Gas Detector | IC- | FGD-2001C | FGD-2001C | JBF-A-2110 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
719 | RD-1T-2-FA | FGD-2002C | Flammable Gas Detector | IC- | FGD-2002C | FGD-2002C | JBF-A-2110 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
720 | RD-1T-2-FA | FGD-2003C | Flammable Gas Detector | IC- | FGD-2003C | FGD-2003C | JBF-A-2110 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
721 | RD-1T-2-FA | TGD-2001C | Toxic Gas Detector | IC- | TGD-2001C | TGD-2001C | JBF-A-2110 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
722 | RD-1T-2-FA | TGD-2002C | Toxic Gas Detector | IC- | TGD-2002C | TGD-2002C | JBF-A-2110 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
723 | RD-1T-2-FA | TGD-2003C | Toxic Gas Detector | IC- | TGD-2003C | TGD-2003C | JBF-A-2110 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
724 | RD-12T-1-FA | JBF-A-2110 | Junction Box | MC- | JBF-A-2110 | JBF-A-2110 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 350 | M40 | MODIFIED
725 | RD-1T-2-FA | FD-2003C | Flame Detector | IC- | FD-2003C | FD-2003C | JBF-A-2111 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
726 | RD-1T-2-FA | FD-2004C | Flame Detector | IC- | FD-2004C | FD-2004C | JBF-A-2111 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
727 | RD-1T-2-FA | FGD-2007C | Flammable Gas Detector | IC- | FGD-2007C | FGD-2007C | JBF-A-2111 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
728 | RD-1T-2-FA | FGD-2008C | Flammable Gas Detector | IC- | FGD-2008C | FGD-2008C | JBF-A-2111 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
729 | RD-1T-2-FA | FGD-2009C | Flammable Gas Detector | IC- | FGD-2009C | FGD-2009C | JBF-A-2111 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
730 | RD-1T-2-FA | TGD-2007C | Toxic Gas Detector | IC- | TGD-2007C | TGD-2007C | JBF-A-2111 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
731 | RD-1T-2-FA | TGD-2008C | Toxic Gas Detector | IC- | TGD-2008C | TGD-2008C | JBF-A-2111 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
732 | RD-1T-2-FA | TGD-2009C | Toxic Gas Detector | IC- | TGD-2009C | TGD-2009C | JBF-A-2111 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
733 | RD-12T-1-FA | JBF-A-2111 | Junction Box | MC- | JBF-A-2111 | JBF-A-2111 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 350 | M40 | MODIFIED
734 | RD-1T-2-FA | FGD-2004C | Flammable Gas Detector | IC- | FGD-2004C | FGD-2004C | JBF-A-2112 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
735 | RD-1T-2-FA | FGD-2005C | Flammable Gas Detector | IC- | FGD-2005C | FGD-2005C | JBF-A-2112 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
736 | RD-1T-2-FA | FGD-2006C | Flammable Gas Detector | IC- | FGD-2006C | FGD-2006C | JBF-A-2112 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
737 | RD-1T-2-FA | TGD-2004C | Toxic Gas Detector | IC- | TGD-2004C | TGD-2004C | JBF-A-2112 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
738 | RD-1T-2-FA | TGD-2005C | Toxic Gas Detector | IC- | TGD-2005C | TGD-2005C | JBF-A-2112 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
739 | RD-1T-2-FA | TGD-2006C | Toxic Gas Detector | IC- | TGD-2006C | TGD-2006C | JBF-A-2112 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
740 | RD-12T-1-FA | JBF-A-2112 | Junction Box | MC- | JBF-A-2112 | JBF-A-2112 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 420 | M40 | MODIFIED
741 | RD-1T-2-FA | FGD-3001 | Flammable Gas Detector | IC- | FGD-3001 | FGD-3001 | JBF-A-2113 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
742 | RD-1T-2-FA | FGD-3002 | Flammable Gas Detector | IC- | FGD-3002 | FGD-3002 | JBF-A-2113 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
743 | RD-1T-2-FA | FGD-3003 | Flammable Gas Detector | IC- | FGD-3003 | FGD-3003 | JBF-A-2113 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
744 | RD-1T-2-FA | TGD-3001 | Toxic Gas Detector | IC- | TGD-3001 | TGD-3001 | JBF-A-2113 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
745 | RD-1T-2-FA | TGD-3002 | Toxic Gas Detector | IC- | TGD-3002 | TGD-3002 | JBF-A-2113 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
746 | RD-1T-2-FA | TGD-3003 | Toxic Gas Detector | IC- | TGD-3003 | TGD-3003 | JBF-A-2113 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
747 | RD-12T-1-FA | JBF-A-2113 | Junction Box | MC- | JBF-A-2113 | JBF-A-2113 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 370 | M40 | MODIFIED
748 | RD-1T-2-FA | FGD-3004 | Flammable Gas Detector | IC- | FGD-3004 | FGD-3004 | JBF-A-2114 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
749 | RD-1T-2-FA | FGD-3005 | Flammable Gas Detector | IC- | FGD-3005 | FGD-3005 | JBF-A-2114 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
750 | RD-1T-2-FA | FGD-3006 | Flammable Gas Detector | IC- | FGD-3006 | FGD-3006 | JBF-A-2114 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
751 | RD-1T-2-FA | FGD-3007 | Flammable Gas Detector | IC- | FGD-3007 | FGD-3007 | JBF-A-2114 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
752 | RD-1T-2-FA | TGD-3004 | Toxic Gas Detector | IC- | TGD-3004 | TGD-3004 | JBF-A-2114 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
753 | RD-1T-2-FA | TGD-3005 | Toxic Gas Detector | IC- | TGD-3005 | TGD-3005 | JBF-A-2114 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | MODIFIED
754 | RD-1T-2-FA | TGD-3006 | Toxic Gas Detector | IC- | TGD-3006 | TGD-3006 | JBF-A-2114 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
755 | RD-1T-2-FA | TGD-3007 | Toxic Gas Detector | IC- | TGD-3007 | TGD-3007 | JBF-A-2114 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
756 | RD-12T-1-FA | JBF-A-2114 | Junction Box | MC- | JBF-A-2114 | JBF-A-2114 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 500 | M40 | MODIFIED
757 | RD-1T-2-FA | FGD-1101 | Flammable Gas Detector | IC- | FGD-1101 | FGD-1101 | JBF-A-2115 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
758 | RD-1T-2-FA | FGD-1102 | Flammable Gas Detector | IC- | FGD-1102 | FGD-1102 | JBF-A-2115 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
759 | RD-1T-2-FA | FGD-1103 | Flammable Gas Detector | IC- | FGD-1103 | FGD-1103 | JBF-A-2115 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
760 | RD-1T-2-FA | TGD-1101 | Toxic Gas Detector | IC- | TGD-1101 | TGD-1101 | JBF-A-2115 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
761 | RD-1T-2-FA | TGD-1102 | Toxic Gas Detector | IC- | TGD-1102 | TGD-1102 | JBF-A-2115 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
762 | RD-1T-2-FA | TGD-1103 | Toxic Gas Detector | IC- | TGD-1103 | TGD-1103 | JBF-A-2115 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
763 | RD-12T-1-FA | JBF-A-2115 | Junction Box | MC- | JBF-A-2115 | JBF-A-2115 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | LT. Blue / Red Strip | NOTE 3 | 300/500 V | 50 | M40 | MODIFIED
764 | RD-1T-2-FA | FGD-1201 | Flammable Gas Detector | IC- | FGD-1201 | FGD-1201 | JBF-A-2116 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
765 | RD-1T-2-FA | FGD-1202 | Flammable Gas Detector | IC- | FGD-1202 | FGD-1202 | JBF-A-2116 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
766 | RD-1T-2-FA | FGD-1203 | Flammable Gas Detector | IC- | FGD-1203 | FGD-1203 | JBF-A-2116 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
767 | RD-1T-2-FA | TGD-1201 | Toxic Gas Detector | IC- | TGD-1201 | TGD-1201 | JBF-A-2116 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
768 | RD-1T-2-FA | TGD-1202 | Toxic Gas Detector | IC- | TGD-1202 | TGD-1202 | JBF-A-2116 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
769 | RD-1T-2-FA | TGD-1203 | Toxic Gas Detector | IC- | TGD-1203 | TGD-1203 | JBF-A-2116 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
770 | RD-12T-1-FA | JBF-A-2116 | Junction Box | MC- | JBF-A-2116 | JBF-A-2116 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 80 | M40
771 | RD-1T-2-FA | HGD-1101 | Hydrogen Gas Detector | IC- | HGD-1101 | HGD-1101 | JBF-A-2117 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
772 | RD-1T-2-FA | HGD-1102 | Hydrogen Gas Detector | IC- | HGD-1102 | HGD-1102 | JBF-A-2117 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
773 | RD-1T-2-FA | HGD-1103 | Hydrogen Gas Detector | IC- | HGD-1103 | HGD-1103 | JBF-A-2117 | FRS | SWA | IS | 1 | Triad | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
774 | RD-12T-1-FA | JBF-A-2117 | Junction Box | MC- | JBF-A-2117 | JBF-A-2117 | FGS | FRS | SWA | IS | 12 | Triad | 1 | Individual & Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32
775 | RD-1P-2-FA | MAC-1001 | Manual Call Point | IC- | MAC-1001 | MAC-1001 | JBF-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
776 | RD-1P-2-FA | MAC-1002 | Manual Call Point | IC- | MAC-1002 | MAC-1002 | JBF-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
777 | RD-1P-2-FA | LHD-1001 | Linear Heat Detector | IC- | LHD-1001 | LHD-1001 | JBF-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
778 | RD-1P-2-FA | LHD-1002 | Linear Heat Detector | IC- | LHD-1002 | LHD-1002 | JBF-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
779 | RD-1P-2-FA | LHD-1003 | Linear Heat Detector | IC- | LHD-1003 | LHD-1003 | JBF-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
780 | RD-1P-2-FA | LHD-1004 | Linear Heat Detector | IC- | LHD-1004 | LHD-1004 | JBF-D-2101 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
781 | RD-12P-1-FA | JBF-D-2101 | Junction Box | MC- | JBF-D-2101 | JBF-D-2101 | FGS | FRS | SWA | NIS | 12 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 270 | M40
782 | RD-1P-2-FA | MAC-2001 | Manual Call Point | IC- | MAC-2001 | MAC-2001 | JBF-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
783 | RD-1P-2-FA | MAC-2003 | Manual Call Point | IC- | MAC-2003 | MAC-2003 | JBF-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
784 | RD-1P-2-FA | LHD-1005 | Linear Heat Detector | IC- | LHD-1005 | LHD-1005 | JBF-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
785 | RD-1P-2-FA | LHD-1006 | Linear Heat Detector | IC- | LHD-1006 | LHD-1006 | JBF-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
786 | RD-1P-2-FA | LHD-1007 | Linear Heat Detector | IC- | LHD-1007 | LHD-1007 | JBF-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
787 | RD-1P-2-FA | LHD-1008 | Linear Heat Detector | IC- | LHD-1008 | LHD-1008 | JBF-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
788 | RD-1P-2-FA | LHD-1009 | Linear Heat Detector | IC- | LHD-1009 | LHD-1009 | JBF-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
789 | RD-1P-2-FA | LHD-1010 | Linear Heat Detector | IC- | LHD-1010 | LHD-1010 | JBF-D-2102 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
790 | RD-12P-1-FA | JBF-D-2102 | Junction Box | MC- | JBF-D-2102 | JBF-D-2102 | FGS | FRS | SWA | NIS | 12 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 250 | M40
791 | RD-1P-2-FA | MAC-3001 | Manual Call Point | IC- | MAC-3001 | MAC-3001 | JBF-D-2103 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
792 | RD-1P-2-FA | MAC-3003 | Manual Call Point | IC- | MAC-3003 | MAC-3003 | JBF-D-2103 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
793 | RD-7P-1-FA | JBF-D-2103 | Junction Box | MC- | JBF-D-2103 | JBF-D-2103 | FGS | FRS | SWA | IS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 500 | M32
794 | RD-1P-2-FA | MAC-2002 | Manual Call Point | IC- | MAC-2002 | MAC-2002 | JBF-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
795 | RD-1P-2-FA | MAC-3002 | Manual Call Point | IC- | MAC-3002 | MAC-3002 | JBF-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
796 | RD-1P-2-FA | MAC-3004 | Manual Call Point | IC- | MAC-3004 | MAC-3004 | JBF-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
797 | RD-1P-2-FA | LHD-3001 | Linear Heat Detector | IC- | LHD-3001 | LHD-3001 | JBF-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
798 | RD-1P-2-FA | LHD-3002 | Linear Heat Detector | IC- | LHD-3002 | LHD-3002 | JBF-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
799 | RD-1P-2-FA | LHD-3003 | Linear Heat Detector | IC- | LHD-3003 | LHD-3003 | JBF-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
800 | RD-1P-2-FA | LHD-3004 | Linear Heat Detector | IC- | LHD-3004 | LHD-3004 | JBF-D-2104 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
801 | RD-12P-1-FA | JBF-D-2104 | Junction Box | MC- | JBF-D-2104 | JBF-D-2104 | FGS | FRS | SWA | NIS | 12 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 400 | M40
802 | RD-1P-2-FA | MAC-4001 | Manual Call Point | IC- | MAC-4001 | MAC-4001 | JBF-D-2105 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
803 | RD-1P-2-FA | MAC-4002 | Manual Call Point | IC- | MAC-4002 | MAC-4002 | JBF-D-2105 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
804 | RD-1P-2-FA | LHD-4001 | Linear Heat Detector | IC- | LHD-4001 | LHD-4001 | JBF-D-2105 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
805 | RD-1P-2-FA | LHD-4002 | Linear Heat Detector | IC- | LHD-4002 | LHD-4002 | JBF-D-2105 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20
806 | RD-7P-1-FA | JBF-D-2105 | Junction Box | MC- | JBF-D-2105 | JBF-D-2105 | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 250 | M32
807 | RD-1P-2-FA | SD-1110 | Smoke Detector | IC- | SD-1110 | SD-1110 | JBF-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
808 | RD-1P-2-FA | SD-1111 | Smoke Detector | IC- | SD-1111 | SD-1111 | JBF-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
809 | RD-1P-2-FA | SD-1112 | Smoke Detector | IC- | SD-1112 | SD-1112 | JBF-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
810 | RD-1P-2-FA | SD-1113 | Smoke Detector | IC- | SD-1113 | SD-1113 | JBF-D-2106 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
811 | RD-7P-1-FA | JBF-D-2106 | Junction Box | MC- | JBF-D-2106 | JBF-D-2106 | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32
812 | RD-1P-2-FA | LSLL-2301 | Low Low Level Alarm | IC- | LSLL-2301 | LSLL-2301 | JBF-D-2107 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
813 | RD-1P-2-FA | LSLL-2302 | Low Low Level Alarm | IC- | LSLL-2302 | LSLL-2302 | JBF-D-2107 | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 15 | M20 | ADDED
814 | RD-7P-1-FA | JBF-D-2107 | Junction Box | MC- | JBF-D-2107 | JBF-D-2107 | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 300 | M32
815 | RD-7P-1-FA | HN-1001 | Horn | MC- | HN-1001 | HN-1001 | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 300 | M32
816 |  | BR-1001 | Beacon - Red
817 |  | BB-1001 | Beacon - Blue
818 | RD-7P-1-FA | HN-2001 | Horn | MC- | HN-2001 | HN-2001 | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 340 | M32
819 |  | BR-2001 | Beacon - Red
820 |  | BB-2001 | Beacon - Blue
821 | RD-7P-1-FA | HN-3001 | Horn | MC- | HN-3001 | HN-3001 | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 340 | M32
822 |  | BR-3001 | Beacon - Red
823 |  | BB-3001 | Beacon - Blue
824 | RD-7P-1-FA | HN-4001 | Horn | MC- | HN-4001 | HN-4001 | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 340 | M32
825 |  | BR-4001 | Beacon - Red
826 |  | BB-4001 | Beacon - Blue
827 | RD-7P-1-F | ESD0-FG-1101 | ESD 0 Request | MC- | FGS-ESD | FGS | ESD | FRS | - | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32 | ADDED
828 |  | ESD1A-FG-1101 | ESD 1A Request | [16 empty] | ADDED
829 |  | ESD2A-FG-1101A | ESD 2A(Train A) Request | [16 empty] | ADDED
830 |  | ESD2A-FG-1101B | ESD 2A(Train B) Request | [16 empty] | ADDED
831 |  | ESD2A-FG-1101C | ESD 2A(Train C) Request | [16 empty] | ADDED
832 | RD-1P-2-FA | FAN-FG-1101 | Battery Room Standby Fan Activation | MC- | FAN-FG-1101 | FGS | IRP | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32 | ADDED
833 | RD-1P-2-FA | INB-FG-1101 | Inhibit to Boost for UPS Charger | MC- | INB-FG-1101 | FGS | UPS | FRS | SWA | NIS | 1 | PAIR | 1.5 | Overall Screen | Red | NOTE 3 |  | 50 | M32 | ADDED
834 | RD-7P-1-F | Ex-FG-G-1101 | FGS System confirmed Gas Alarm to Existing FGS | MC- | FGS-EX FGS | FGS | EXISTING FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32 | ADDED
835 |  | Ex-FG-F-1101 | FGS System confirmed Fire Alarm to Existing FGS System | [16 empty] | ADDED
836 |  | Ex-FG-G-1102 | Existing FGS confirmed Gas Alarm to FGS System | [16 empty] | ADDED
837 |  | Ex-FG-F-1102 | Existing FGS confirmed Fire Alarm to FGS System | [16 empty] | ADDED
838 | RD-7P-1-FA | HSS-2301A | Pump Start Command | MC- | P-2301A | LCP-P-2301A | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32 | ADDED
839 |  | XL-2301A | Pump Local/ Remote Status | [16 empty] | ADDED
840 |  | XR-2301A | Pump Running/ Stopped Status | [16 empty] | ADDED
841 |  | XF-2301A | Pump Fault Status | [16 empty] | ADDED
842 |  | PAL-2301A | Low Pressure Alarm | [16 empty] | ADDED
843 | RD-7P-1-FA | HSS-2301B | Pump Start Command | MC- | P-2301B | LCP-P-2301B | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32 | ADDED
844 |  | XL-2301B | Pump Local/ Remote Status | [16 empty] | ADDED
845 |  | XR-2301B | Pump Running/ Stopped Status | [16 empty] | ADDED
846 |  | XF-2301B | Pump Fault Status | [16 empty] | ADDED
847 |  | PAL-2301B | Low Pressure Alarm | [16 empty] | ADDED
848 | RD-7P-1-FA | HSS-2302A | Pump Start Command | MC- | P-2302A | LCP-P-2302A | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32 | ADDED
849 |  | XL-2302A | Pump Local/ Remote Status | [16 empty] | ADDED
850 |  | XR-2302A | Pump Running/ Stopped Status | [16 empty] | ADDED
851 |  | XF-2302A | Pump Fault Status | [16 empty] | ADDED
852 |  | PAL-2302A | Low Pressure Alarm | [16 empty] | ADDED
853 | RD-7P-1-FA | HSS-2302B | Pump Start Command | MC- | P-2302B | LCP-P-2302B | FGS | FRS | SWA | NIS | 7 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32 | ADDED
854 |  | XL-2302B | Pump Local/ Remote Status | [16 empty] | ADDED
855 |  | XR-2302B | Pump Running/ Stopped Status | [16 empty] | ADDED
856 |  | XF-2302B | Pump Fault Status | [16 empty] | ADDED
857 |  | PAL-2302B | Low Pressure Alarm | [16 empty] | ADDED
858 | RD-20P-1-F | LAMP-ACB-FD | Fire Alarm Lamp for Control Building | MC- | FGS Matrix1 | FGS | FGS Matrix | FRS | - | NIS | 20 | PAIR | 1 | Overall Screen | Gray / Red Strip | NOTE 3 | 300/500 V | 50 | M50 | ADDED
859 |  | LAMP-TGCA-FD | Fire Alarm Lamp for Turbo Comp. A | [16 empty] | ADDED
860 |  | LAMP-TGCB-FD | Fire Alarm Lamp for Turbo Comp. B | [16 empty] | ADDED
861 |  | LAMP-TGCC-FD | Fire Alarm Lamp for Turbo Comp. C | [16 empty] | ADDED
862 |  | LAMP-AC-FD | Fire Alarm Lamp for Electrical Building | [16 empty] | ADDED
863 |  | LAMP-MVSG-FD | Fire Alarm Lamp for Utility Area | [16 empty] | ADDED
864 |  | LAMP-TCA-FGD | FGD Alarm Lamp for Turbo Comp. A | [16 empty] | ADDED
865 |  | LAMP-TCB-FGD | FGD Alarm Lamp for Turbo Comp. B | [16 empty] | ADDED
866 |  | LAMP-TCC-FGD | FGD Alarm Lamp for Turbo Comp. C | [16 empty] | ADDED
867 |  | LAMP-GCA-FGD | FGD Alarm Lamp for Gas Cooler A | [16 empty] | ADDED
868 |  | LAMP-GCB-FGD | FGD Alarm Lamp for Gas Cooler B | [16 empty] | ADDED
869 |  | LAMP-GCC-FGD | FGD Alarm Lamp for Gas Cooler C | [16 empty] | ADDED
870 |  | LAMP-SCA-FGD | FGD Alarm Lamp for Scrubber A | [16 empty] | ADDED
871 |  | LAMP-SCAB-FGD | FGD Alarm Lamp for Scrubber B | [16 empty] | ADDED
872 |  | LAMP-SCC-FGD | FGD Alarm Lamp for Scrubber C | [16 empty] | ADDED
873 |  | LAMP-CR-FGD | FGD Alarm Lamp for Control Building AIR Entrance | [16 empty] | ADDED
874 | RD-20P-1-F | LAMP-EB-FGD | FGD Alarm Lamp for Electrical Building | MC- | FGS Matrix2 | FGS | FGS Matrix | FRS | - | NIS | 20 | PAIR | 1 | Overall Screen | Red | NOTE 3 | 300/500 V | 50 | M32 | ADDED
875 |  | LAMP-PA-FGD | FGD Alarm Lamp for Utility Area | [16 empty] | ADDED
876 |  | LAMP-BR-HGD | Hydrogen Gas Alarm Lamp for Battery Room | [16 empty] | ADDED
877 |  | LAMP-TCA-TGD | TGD Alarm Lamp for Turbo Comp. A | [16 empty] | ADDED
878 |  | LAMP-TCB-TGD | TGD Alarm Lamp for Turbo Comp. B | [16 empty] | ADDED
879 |  | LAMP-TCC-TGD | TGD Alarm Lamp for Turbo Comp. C | [16 empty] | ADDED
880 |  | LAMP-GCA-TGD | TGD Alarm Lamp for Gas Cooler A | [16 empty] | ADDED
881 |  | LAMP-GCB-TGD | TGD Alarm Lamp for Gas Cooler B | [16 empty] | ADDED
882 |  | LAMP-GCC-TGD | TGD Alarm Lamp for Gas Cooler C | [16 empty] | ADDED
883 |  | LAMP-SCA-TGD | TGD Alarm Lamp for Scrubber A | [16 empty] | ADDED
884 |  | LAMP-SCAB-TGD | TGD Alarm Lamp for Scrubber B | [16 empty] | ADDED
885 |  | LAMP-SCC-TGD | TGD Alarm Lamp for Scrubber C | [16 empty] | ADDED
886 |  | LAMP-CR-TGD | TGD Alarm Lamp for Control Building AIR Entrance | [16 empty] | ADDED
887 |  | LAMP-EB-TGD | TGD Alarm Lamp for Electrical Building | [16 empty] | ADDED
888 |  | LAMP-PA-TGD | TGD Alarm Lamp for Utility Area | [16 empty] | ADDED
889 | RD-1P-2-F | FACP | Output Port of Loop 1 | IC- | FACP | FACP | HN-1102 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 1 ADDED
890 | RD-1P-2-F | HN-1102 | Horn | IC- | HN-1102 | HN-1102 | BR-1102 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
891 | RD-1P-2-F | BR-1102 | Beacon - Red | IC- | BR-1102 | BR-1102 | BB-1102 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
892 | RD-1P-2-F | BB-1102 | Beacon - Blue | IC- | BB-1102 | BB-1102 | MAC-1101 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
893 | RD-1P-2-F | MAC-1101 | Manual Call Point | IC- | MAC-1101 | MAC-1101 | SD-1101 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
894 | RD-1P-2-F | SD-1101 | Smoke Detector | IC- | SD-1101 | SD-1101 | SD-1102 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
895 | RD-1P-2-F | SD-1102 | Smoke Detector | IC- | SD-1102 | SD-1102 | SD-1103 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
896 | RD-1P-2-F | SD-1103 | Smoke Detector | IC- | SD-1103 | SD-1103 | SD-1104 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
897 | RD-1P-2-F | SD-1104 | Smoke Detector | IC- | SD-1104 | SD-1104 | SD-1107 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
898 | RD-1P-2-F | SD-1107 | Smoke Detector | IC- | SD-1107 | SD-1107 | SD-1106 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
899 | RD-1P-2-F | SD-1106 | Smoke Detector | IC- | SD-1106 | SD-1106 | SD-1105 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
900 | RD-1P-2-F | SD-1105 | Smoke Detector | IC- | SD-1105 | SD-1105 | MAC-1102 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
901 | RD-1P-2-F | MAC-1102 | Manual Call Point | IC- | MAC-1102 | MAC-1102 | BL-1101 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
902 | RD-1P-2-F | BL-1101 | Bell | IC- | BL-1101 | BL-1101 | SD-1108 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
903 | RD-1P-2-F | SD-1108 | Smoke Detector | IC- | SD-1108 | SD-1108 | SD-1109 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
904 | RD-1P-2-F | SD-1109 | Smoke Detector | IC- | SD-1109 | SD-1109 | SD-1116 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
905 | RD-1P-2-F | SD-1116 | Smoke Detector | IC- | SD-1116 | SD-1116 | SD-1117 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
906 | RD-1P-2-F | SD-1117 | Smoke Detector | IC- | SD-1117 | SD-1117 | MAC-1107 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
907 | RD-1P-2-F | MAC-1107 | Manual Call Point | IC- | MAC-1107 | MAC-1107 | HN-1101 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
908 | RD-1P-2-F | HN-1101 | Horn | IC- | HN-1101 | HN-1101 | BR-1101 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
909 | RD-1P-2-F | BR-1101 | Beacon - Red | IC- | BR-1101 | BR-1101 | BB-1101 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
910 | RD-1P-2-F | BB-1101 | Beacon - Blue | IC- | BB-1101 | BB-1101 | SD-1115 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
911 | RD-1P-2-F | SD-1115 | Smoke Detector | IC- | SD-1115 | SD-1115 | MAC-1104 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
912 | RD-1P-2-F | MAC-1104 | Manual Call Point | IC- | MAC-1104 | MAC-1104 | BL-1103 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
913 | RD-1P-2-F | BL-1103 | Bell | IC- | BL-1103 | BL-1103 | SD-1114 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
914 | RD-1P-2-F | SD-1114 | Smoke Detector | IC- | SD-1114 | SD-1114 | BL-1102 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
915 | RD-1P-2-F | BL-1102 | Bell | IC- | BL-1102 | BL-1102 | MAC-1103 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
916 | RD-1P-2-F | MAC-1103 | Manual Call Point | IC- | MAC-1103 | MAC-1103 | MAC-1106 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
917 | RD-1P-2-F | MAC-1106 | Manual Call Point | IC- | MAC-1106 | MAC-1106 | SD-1121 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
918 | RD-1P-2-F | SD-1121 | Smoke Detector | IC- | SD-1121 | SD-1121 | SD-1122 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
919 | RD-1P-2-F | SD-1122 | Smoke Detector | IC- | SD-1122 | SD-1122 | SD-1123 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
920 | RD-1P-2-F | SD-1123 | Smoke Detector | IC- | SD-1123 | SD-1123 | SD-1124 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
921 | RD-1P-2-F | SD-1124 | Smoke Detector | IC- | SD-1124 | SD-1124 | MAC-1105 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
922 | RD-1P-2-F | MAC-1105 | Manual Call Point | IC- | MAC-1105 | MAC-1105 | SD-1118 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
923 | RD-1P-2-F | SD-1118 | Smoke Detector | IC- | SD-1118 | SD-1118 | SD-1119 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
924 | RD-1P-2-F | SD-1119 | Smoke Detector | IC- | SD-1119 | SD-1119 | SD-1120 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 5 | M20 | LOOP 1 ADDED
925 | RD-1P-2-F | SD-1120 | Smoke Detector | IC- | SD-1120 | SD-1120 | FACP | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 1 ADDED
926 | RD-1P-2-F | FACP | Output Port of Loop 2 | IC- | FACP | FACP | SD-1181 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 2 ADDED
927 | RD-1P-2-F | SD-1181 | Smoke Detector | IC- | SD-1181 | SD-1181 | SD-1182 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 2 ADDED
928 | RD-1P-2-F | SD-1182 | Smoke Detector | IC- | SD-1182 | SD-1182 | SD-1183 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 2 ADDED
929 | RD-1P-2-F | SD-1183 | Smoke Detector | IC- | SD-1183 | SD-1183 | SD-1184 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 2 ADDED
930 | RD-1P-2-F | SD-1184 | Smoke Detector | IC- | SD-1184 | SD-1184 | SD-1187 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 2 ADDED
931 | RD-1P-2-F | SD-1187 | Smoke Detector | IC- | SD-1187 | SD-1187 | SD-1186 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 2 ADDED
932 | RD-1P-2-F | SD-1186 | Smoke Detector | IC- | SD-1186 | SD-1186 | SD-1185 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 2 ADDED
933 | RD-1P-2-F | SD-1185 | Smoke Detector | IC- | SD-1185 | SD-1185 | BL-1103 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 2 ADDED
934 | RD-1P-2-F | BL-1103 | Bell | IC- | BL-1103 | BL-1103 | FACP | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 2 ADDED
935 | RD-1P-2-FA | FACP | Output Port of Loop 3 | IC- | FACP | FACP | HN-1201 | FRS | SWA | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 80 | M20 | LOOP 3 ADDED
936 | RD-1P-2-F | HN-1201 | Horn | IC- | HN-1201 | HN-1201 | BR-1201 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 3 ADDED
937 | RD-1P-2-F | BR-1201 | Beacon - Red | IC- | BR-1201 | BR-1201 | BB-1201 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 3 ADDED
938 | RD-1P-2-F | BB-1201 | Beacon - Blue | IC- | BB-1201 | BB-1201 | MAC-1201 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 3 ADDED
939 | RD-1P-2-F | MAC-1201 | Manual Call Point | IC- | MAC-1201 | MAC-1201 | SD-1201 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 3 ADDED
940 | RD-1P-2-F | SD-1201 | Smoke Detector | IC- | SD-1201 | SD-1201 | SD-1202 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 3 ADDED
941 | RD-1P-2-F | SD-1202 | Smoke Detector | IC- | SD-1202 | SD-1202 | MAC-1202 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 3 ADDED
942 | RD-1P-2-FA | MAC-1202 | Manual Call Point | IC- | MAC-1202 | MAC-1202 | FACP | FRS | SWA | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 80 | M20 | LOOP 3 ADDED
943 | RD-1P-2-FA | FACP | Output Port of Loop 4 | IC- | FACP | FACP | HN-1202 | FRS | SWA | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 80 | M20 | LOOP 4 ADDED
944 | RD-1P-2-F | HN-1202 | Horn | IC- | HN-1202 | HN-1202 | BR-1202 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 4 ADDED
945 | RD-1P-2-F | BR-1202 | Beacon - Red | IC- | BR-1202 | BR-1202 | BB-1202 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 4 ADDED
946 | RD-1P-2-F | BB-1202 | Beacon - Blue | IC- | BB-1202 | BB-1202 | MAC-1203 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 4 ADDED
947 | RD-1P-2-F | MAC-1203 | Manual Call Point | IC- | MAC-1203 | MAC-1203 | LHD-1201 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 4 ADDED
948 | RD-1P-2-F | LHD-1201 | Linear Heat Detector | IC- | LHD-1201 | LHD-1201 | LHD-1202 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 4 ADDED
949 | RD-1P-2-F | LHD-1202 | Linear Heat Detector | IC- | LHD-1202 | LHD-1202 | LHD-1203 | FRS | - | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 20 | M20 | LOOP 4 ADDED
950 | RD-1P-2-FA | LHD-1203 | Linear Heat Detector | IC- | LHD-1203 | LHD-1203 | FACP | FRS | SWA | - | 1 | Pair | 1.5 | Overall Screen | Red | Note 3 | 300/500 V | 80 | M20 | LOOP 4 ADDED
951 | SERIAL LINK | XA-CO2-1101 | MANUAL/AUTO SELECTOR SWITCH STATUS (FOR PROTECTED AREA) | IC- | FACP | FACP | CO2 PACKAGE | - | - | - | - | - | - | - | - | - | - | 50 | - | ADDED
952 |  | XRE-CO2-1101 | RELEASED STATUS (FOR PROTECTED AREA) | [16 empty] | ADDED
953 |  | XI-CO2-1101 | INHIBIT STATUS (FOR PROTECTED AREA) | [16 empty] | ADDED
954 |  | XF-CO2-1101 | GENERAL FAULT | [16 empty] | ADDED
955 |  | HS-CO2-1101 | AUTOMAT RELEASE COMMAND (FOR PROTECTED AREA) | [16 empty] | ADDED
D01
TOTALLY REVIZED