## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-PEDCO-120-IN-LI-0005_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0587 |  |  | Transmital Date: 13 Feb 2022
Document Title: Panels & Junction Box List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-IN-TR-0587 |  |  | Transmital Date: 13 Feb 2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-IN-LI-0005_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به اينكه مدارك پيش نياز و مرتبط با اين مدرك مانند I/O و Termination Digram داراي كامنت و يا تاييد نشده است، اين مدرك قابل بررسي نمي باشد. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | همه کامنت های مدارک پیش نیاز بر طرف گردیده و مدارک همسان سازی گردید
2 | بنا بر بند 13 پيمان و همچنين كامنت شماره 1، هر گونه تبعات مالي و زماني بر عهده پيمانكار مي باشد. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | درخواست کارفرمای محترم مد نظر قرار می گیرد.
2 | هر گونه تغييري در مدارك مرتبط در اين مدرك اعمال و اصلاح گردد |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | درخواست کارفرمای محترم مد نظر قرار می گیرد.
3 | بنظر مي رسد كه يك عدد كنترل پنل براي تمامي كمپرسورها (A/B/C) در نظر گرفته شده است، اين مورد اصلا قابل قبول نمي باشد. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | در همه مدارک برای تمامی کمپرسور (A/B/C) , و با توجه به دیتا شیت کمپرسور ها و PID مربوطه یک عدد پنل CPU در نظر گرفته شده و از سوی کارفرما کامنتی مبنی بر اینکه برای هر کمپرسور جداگانه پنل CPU در نظر گرفته شود قید نشده است.
4 | با توجه به عنوان مدرك، تمام پنل هايي كه با سيستم هاي اصلي DCS/ESD/F&G سيگنال/ارتباط واسط دارند در نظر گرفته شود. (CO2/HVAC/FACP/LCP/Consoles/Packages….) |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | مدرک اصلاح گردید.
5 | در مورد ديتكتورهاي داخل ساختمان (بصورت HW) نيز شفاف سازي صورت پذيرد. ارتباطات در نظر گرفته نشده است. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | ارتباطات در مدرک Instrument Cable list ذکر شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 26 Feb 2022 |  |  |  |  | Date: