## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-SSGRL-PEDCO-110-IN-DG-0002 |  |  |  |  | EPC Contractor Tr. No.:BK-HD-PEDCO-T-0369 |  |  | Transmittal Date: 20 Dec 2021
Document Title:WHCP Hydraulic Diagrams - Wellheads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0008-IN-TR-0369 |  |  | Transmital Date: 20 Dec 2021
[5 empty] | CRS No:PEDCO-CRS-BK-SSGRL-PEDCO-110-IN-DG-0002_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Note that WHCP indicators and push bottoms will be finalized based on Client requirement and vendor recommendation. |  | BK-SUR-ENG-INS-00-02064 | 2021-11-21 | Noted. Dedicated Note has been added. (This comment has been noted in last revision of document )
2 | The quantity and configuration of N2 banks shall be followed based on specification for wellhead control panel. |  | BK-SUR-ENG-INS-00-02064 | 2021-11-21 | Noted. Dedicated Note has been added. (This comment has been noted in last revision of document )
3 | scope of supply for Pressure switches shall be specified, if they are supplied by vendor. |  | BK-SUR-ENG-INS-00-02064 | 2021-11-21 | Noted. Dedicated Note has been added. (This comment has been noted in last revision of document )
4 | hydraulic connection between switches and WHCP shall be shown. |  | BK-SUR-ENG-INS-00-02064 | 2021-11-21 | High low switches are located inside panel. Location will be specified by vendor. (This comment has been noted in last revision of document )
5 | Note 8 to be clarified. |  | BK-SUR-ENG-INS-00-02064 | 2021-11-21 | As per specification required logic for indicating First trip cause to be implemented. (This comment has been noted in last revision of document )
6 | This document is not compatible with related P&IDs. Integrity between related documents shall be considered. |  | BK-SUR-ENG-INS-00-02064 | 2021-11-21 | Modified as per the latest P&ID (This comment has been noted in last revision of document )
7 | Standard legend for pneumatic lines to be considered. |  | BK-SUR-ENG-INS-00-02064 | 2021-11-21 | Noted. (This comment has been noted in last revision of document )
8 | Regarding to documents notes, documents will be finalized later according to vendor design so drawing shall be issued after that |  | BK-SUR-ENG-INS-00-02502 | 2022-01-01 | this document is an attachment for contract so shall be issued before PO . It shall be considered that this document is designed and prepared refer to the latest version of reference documents.
9 | to avoid any discrepancy with other documents shut down push buttom (on the fence) shall be shown or referred (as note or drawing) |  | BK-SUR-ENG-INS-00-02502 | 2022-01-01 | Refer to project's basic documents, PB on fence is not required.
10 | regarding to note 3, process data shall be rechecked to final conformation |  | BK-SUR-ENG-INS-00-02502 | 2022-01-01 | Noted.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and inculpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 01 Jan 2021 |  |  |  |  | Date: