## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 9
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | EL | LI | 0002 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL POWER & CONTROL CABLE SCHEDULE نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | June.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-709067
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 9
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | LI | 0002 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 51
2 | X | [7 empty] | 52
3 | X | [7 empty] | 53
4 | X | [7 empty] | 54
5 | X | [7 empty] | 55
6 | X | [7 empty] | 56
7 | X | [7 empty] | 57
8 | X | [7 empty] | 58
9 | X | [7 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## LEGEND
1. ELECTRICAL CABLE NUMBERING SYSTEM
XXX-XXXXX- XX- XX 1 2 3
(1) 1ST GROUP (EQUIPMENT NUMBER)
(2) 2ND GROUP (CABLE TYPE COMMODITY CODE):
HP: HIGH VOLTAGE POWER CABLE (20 KV & ABOVE)
MP: MEDIUM VOLTAGE POWER CABLE (6 KV & ABOVE)
LP: LOW VOLTAGE POWER CABLE (VOLTAGE LESS THAN 1KV)
SH: CABLE FOR MOTOR SPACE HEATER
CS: CABLE FOR LOCAL CONTROL STATION
CT: CURRENT CABLES
C: CONTROL CABLES
(3) SERIAL NO.
2. CABLE TYPE
MV Power Cables (Armoured) | LV Power Cables | Control Cables
(a) Cable Voltage | (a) Armour Type | (b) Armour Type
M1 11 kV | A Armoured | A Armoured
M2 3.3 kV | U Un-Armoured | U Un-Armoured
(b) Lead Cover Type | (b) Lead Cover type | (c) Lead Cover type
L With Lead cover | L With Lead cover | L With Lead cover
N Without Lead cover | N Without Lead cover | N Without Lead cover
(c) Number of Cores | (c) Number of cores | (d) Number of cores
1 Single Core | 1 to 5 | 1 to 30
3 Multi Core | (d) VFD Type
V VFD Cables
None None VFD Cables
Notes:
1- The control cable of IRP Pump will be supplied by vendor
Reference documents are as below:
Area Electrical Cable Route & Section Layout of Well Pads (BK-SSGRL-PEDCO-110-EL-PY-0006)
Electrical Cable Route & Section Layout For Switchgear Building of Well Pads (BK-SSGRL-PEDCO-110-EL-PY-0007)
تسهیلات
ELECTRICAL POWER & CONTROL CABLE SCHEDULE
شماره صفحه: 3 از 9
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
LI
0002
D00
بسته کاری
GCS
پروژه
BK

## GCS
Item | Rev | Cable Tag No. | Service Voltage (KV) | Equipment Tag |  | Rating (KW) | Size | Cable Size (SQMM) |  |  |  | Length (m) | Cable Gland Size |  | O.D (mm) | Cable Type | Description
|  |  |  | From | To |  |  | Core | Phase | N | E |  | Source | Field
1 | D00 | TR-001-MP-01 | 11 | GCS-11-SWG-001A | GCS-TR-001 | 1250KVA | 3×95 | 3C | 95 | - | - | 40 | - | - | 68.8 | M1N3 | Transformer-001 11/.42 KV
2 | D00 | NSWG-001A-LP-A1 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
3 | D00 | NSWG-001A-LP-A2 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
4 | D00 | NSWG-001A-LP-A3 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
5 | D00 | NSWG-001A-LP-A4 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
6 | D00 | NSWG-001A-LP-B1 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
7 | D00 | NSWG-001A-LP-B2 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
8 | D00 | NSWG-001A-LP-B3 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
9 | D00 | NSWG-001A-LP-B4 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
10 | D00 | NSWG-001A-LP-C1 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
11 | D00 | NSWG-001A-LP-C2 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
12 | D00 | NSWG-001A-LP-C3 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
13 | D00 | NSWG-001A-LP-C4 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
14 | D00 | NSWG-001A-LP-N1 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | - | 400 | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
15 | D00 | NSWG-001A-LP-N2 | 0.4 | GCS-TR-001 | GCS-400-NSWG-001A | 1250KVA | 1×400 | 1C | - | 400 | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 001 to LV Switchgear
16 | D00 | NSWG-001A-C-A1 | 0.11DC | GCS-TR-001 | GCS-400-NSWG-001A | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | from Secondary Side of Transformer 001 to LV Switchgear
17 | D00 | TR-002-MP-02 | 11 | GCS-11-SWG-001B | GCS-TR-002 | 1250KVA | 3×95 | 3C | 95 | - | - | 40 | - | - | 68.8 | M1N3 | Transformer-002 11/.42 KV
18 | D00 | NSWG-001B-LP-A1 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
19 | D00 | NSWG-001B-LP-A2 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
20 | D00 | NSWG-001B-LP-A3 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
21 | D00 | NSWG-001B-LP-A4 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
22 | D00 | NSWG-001B-LP-B1 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
23 | D00 | NSWG-001B-LP-B2 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
24 | D00 | NSWG-001B-LP-B3 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
25 | D00 | NSWG-001B-LP-B4 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
26 | D00 | NSWG-001B-LP-C1 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
27 | D00 | NSWG-001B-LP-C2 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
28 | D00 | NSWG-001B-LP-C3 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
29 | D00 | NSWG-001B-LP-C4 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | 400 | - | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
30 | D00 | NSWG-001B-LP-N1 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | - | 400 | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
31 | D00 | NSWG-001B-LP-N2 | 0.4 | GCS-TR-002 | GCS-400-NSWG-001B | 1250KVA | 1×400 | 1C | - | 400 | - | 20 | - | M40 | 39.6 | LAN1 | from Secondary Side of Transformer 002 to LV Switchgear
32 | D00 | NSWG-001B-C-B1 | 0.11DC | GCS-TR-002 | GCS-400-NSWG-001B | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | from Secondary Side of Transformer 002 to LV Switchgear
33 | D00 | SWG-3.3-MP-01 | 11 | GCS-11-SWG-001B | GCS-TR-03 | 800 kVA | 3×70 | 3C | 70 | - | - | 40 | - | - | 64.5 | M1N3 | from Switchgear 11 to Fire Water Transformer
34 | D00 | TR-03-MP-02 | 3.3 | GCS-TR-03 | GCS-3.3-SWG-001 | - | 3×70 | 3C | 70 | - | - | 40 | - | M63 | 64.5 | M2N3 | from Secondary Side of Transformer to Fire Water Electric Pump
35 | D00 | P-2301A-MP-A1 | 3.3 | GCS-3.3-SWG-001 | P-2301A | 300 | 3×70 | 3C | 70 | - | - | 40 | M63 | M63 | 64.5 | M2N3 | Fire Water Electric Pump
36 | D00 | NGR-01-MP-03 | 3.3 | GCS-TR-03 | GCS-3.3-NGR-01 | - | 3×70 | 3C | 70 | - | - | 40 | M63 | M63 | 64.5 | M2N3 | NGR
37 | D00 | NSWG-001A-C-C1 | 0.11DC | GCS-TR-03 | GCS-3.3-SWG-001 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | from Secondary Side of Transformer 03 to 3.3 Switchgear
38 | D00 | C-2101A-MP-A1 | 11 | GCS-11-SWG-001A | C-2101A | 1250 | 3×95 | 3C | 95 | - | - | 250 | M75 | M75 | 75.2 | M1L3 | First & Second Stage Gas Compressor A
39 | D00 | CAP-MP-A2 | 11 | GCS-11-SWG-001A | Cap Bank A | 600 kvar | 3×95 | 3C | 95 | - | - | 40 | M75 | M75 | 75.2 | M1N3 | Capacitor Bank for Gas Compressor A
40 | D00 | C-2101A-C-A3 | 0.11DC | GCS-11-SWG-001A | C-2101A | 1250 | 10×2.5 | 10C | 2.5 | - | - | 250 | M25 | M25 | 22.9 | CAL10 | LCS for Gas Compressor A
41 | D00 | NDP-2101A-LP-01 | 0.4 | GCS-400-NSWG-001A | NDP-2101A | 20 | 3×95+50 | 4C | 95 | 50 | - | 250 | M63 | M63 | 53.8 | LAN4 | Normal Panel for Gas Compressor C-2101A (Auxiliary)
42 | D00 | C-2101A-C-A5 | 0.4 | GCS-11-SWG-001A | C-2101A | - | 10×3PL | 10C | 1.5 | - | - | 250 | M25 | M25 | 19.8 | CAL10 | RTD for Gas Compressor A
43 | D00 | C-2101B-MP-B1 | 11 | GCS-11-SWG-001B | C-2101B | 1250 | 3×95 | 3C | 95 | - | - | 280 | M75 | M75 | 75.2 | MAL3 | First & Second Stage Gas Compressor B
44 | D00 | CAP-MP-B2 | 11 | GCS-11-SWG-001B | Cap Bank B | 600 kvar | 3×95 | 3C | 95 | - | - | 40 | M75 | M75 | 75.2 | MAL3 | Capacitor Bank for Gas Compressor B
45 | D00 | C-2101B-C-B3 | 0.11DC | GCS-11-SWG-001B | C-2101B | 1250 | 10×2.5 | 10C | 2.5 | - | - | 280 | M25 | M25 | 22.9 | CAL10 | LCS for Gas Compressor B
46 | D00 | NDP-2101B-LP-01 | 0.4 | GCS-400-NSWG-001B | NDP-2101B | 20 | 3×120+70 | 4C | 120 | 70 | - | 280 | M63 | M63 | 59.3 | LAN4 | Normal Panel for Gas Compressor C-2101B (Auxiliary)
47 | D00 | C-2101A-C-B5 | 0.4 | GCS-11-SWG-001B | C-2101B | - | 10×3PL | 10C | 1.5 | - | - | 280 | M25 | M25 | 19.8 | CAL10 | RTD for Gas Compressor B
48 | D00 | C-2101C-MP-C1 | 11 | GCS-11-SWG-001A | C-2101C | 1250 | 3×95 | 3C | 95 | - | - | 310 | M75 | M75 | 75.2 | MAL3 | First & Second Stage Gas Compressor C
49 | D00 | CAP-MP-C2 | 11 | GCS-11-SWG-001A | Cap Bank C | 600 kvar | 3×95 | 3C | 95 | - | - | 40 | M75 | M75 | 75.2 | MAL3 | Capacitor Bank for Gas Compressor C
50 | D00 | C-2101C-C-C3 | 0.11DC | GCS-11-SWG-001A | C-2101C | 1250 | 10×2.5 | 10C | 2.5 | - | - | 310 | M25 | M25 | 22.9 | CAL10 | LCS for Gas Compressor C
51 | D00 | NDP-2101C-LP-01 | 0.4 | GCS-400-NSWG-001B | NDP-2101C | 20 | 3×120+70 | 4C | 120 | 70 | - | 310 | M63 | M63 | 59.3 | LAN4 | Normal Panel for Gas Compressor C-2101C (Auxiliary)
52 | D00 | C-2101A-C-C5 | 0.4 | GCS-11-SWG-001A | C-2101C | - | 10×3PL | 10C | 1.5 | - | - | 310 | M25 | M25 | 19.8 | CAL10 | RTD for Gas Compressor C
53 | D00 | AC-2121A-LP-01 | 0.4 | GCS-400-NSWG-001A | AC-2121A | 18.5 | 3×25 | 3C | 25 | - | - | 350 | M32 | M32 | 26.4 | LAL3 | First Stage Air Cooler 21A
54 | D00 | AC-2121A-C-01 | 0.4 | GCS-400-NSWG-001A | AC-2121A | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 21A
55 | D00 | AC-2121A-C-02 | 0.4 | GCS-400-NSWG-001A | AC-2121A | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 21A
56 | D00 | AC-2121A-C-03 | 0.4 | GCS-400-NSWG-001A | AC-2121A | - | 10×2.5 | 10C | 2.5 | - | - | 350 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 21A
57 | D00 | AC-2122A-LP-01 | 0.4 | GCS-400-NSWG-001A | AC-2122A | 18.5 | 3×25 | 3C | 25 | - | - | 350 | M32 | M32 | 26.4 | LAL3 | First Stage Air Cooler 22A
58 | D00 | AC-2122A-C-01 | 0.4 | GCS-400-NSWG-001A | AC-2122A |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 22A
59 | D00 | AC-2122A-C-02 | 0.4 | GCS-400-NSWG-001A | AC-2122A |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 22A
60 | D00 | AC-2122A-C-03 | 0.4 | GCS-400-NSWG-001A | AC-2122A |  | 10×2.5 | 10C | 2.5 | - | - | 350 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 22A
61 | D00 | AC-2121B-LP-01 | 0.4 | GCS-400-NSWG-001B | AC-2121B | 18.5 | 3×25 | 3C | 25 | - | - | 350 | M32 | M32 | 26.4 | LAL3 | First Stage Air Cooler 21B
62 | D00 | AC-2121B-C-01 | 0.4 | GCS-400-NSWG-001B | AC-2121B |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 21B
63 | D00 | AC-2121B-C-02 | 0.4 | GCS-400-NSWG-001B | AC-2121B |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 21B
64 | D00 | AC-2121B-C-03 | 0.4 | GCS-400-NSWG-001B | AC-2121B |  | 10×2.5 | 10C | 2.5 | - | - | 350 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 21B
65 | D00 | AC-2122B-LP-01 | 0.4 | GCS-400-NSWG-001B | AC-2122B | 18.5 | 3×25 | 3C | 25 | - | - | 350 | M32 | M32 | 26.4 | LAL3 | First Stage Air Cooler 22B
66 | D00 | AC-2122B-C-01 | 0.4 | GCS-400-NSWG-001B | AC-2122B |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 22B
67 | D00 | AC-2122B-C-02 | 0.4 | GCS-400-NSWG-001B | AC-2122B |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 22B
68 | D00 | AC-2122B-C-03 | 0.4 | GCS-400-NSWG-001B | AC-2122B |  | 10×2.5 | 10C | 2.5 | - | - | 350 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 22B
69 | D00 | AC-2121C-LP-01 | 0.4 | GCS-400-NSWG-001A | AC-2121C | 18.5 | 3×25 | 3C | 25 | - | - | 390 | M32 | M32 | 26.4 | LAL3 | First Stage Air Cooler 21C
70 | D00 | AC-2121C-C-01 | 0.4 | GCS-400-NSWG-001A | AC-2121C |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 21C
71 | D00 | AC-2121C-C-02 | 0.4 | GCS-400-NSWG-001A | AC-2121C |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 21C
72 | D00 | AC-2121C-C-03 | 0.4 | GCS-400-NSWG-001A | AC-2121C |  | 10×2.5 | 10C | 2.5 | - | - | 390 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 21C
73 | D00 | AC-2122C-LP-01 | 0.4 | GCS-400-NSWG-001A | AC-2122C | 18.5 | 3×25 | 3C | 25 | - | - | 390 | M32 | M32 | 26.4 | LAL3 | First Stage Air Cooler 22C
74 | D00 | AC-2122C-C-01 | 0.4 | GCS-400-NSWG-001A | AC-2122C |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 22C
75 | D00 | AC-2122C-C-02 | 0.4 | GCS-400-NSWG-001A | AC-2122C |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 22C
76 | D00 | AC-2122C-C-03 | 0.4 | GCS-400-NSWG-001A | AC-2122C |  | 10×2.5 | 10C | 2.5 | - | - | 390 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 22C
77 | D00 | AC-2131A-LP-01 | 0.4 | GCS-400-NSWG-001A | AC-2131A | 18.5 | 3×25 | 3C | 25 | - | - | 390 | M32 | M32 | 26.4 | LAL3 | Second Stage Air Cooler 31A
78 | D00 | AC-2131A-C-01 | 0.4 | GCS-400-NSWG-001A | AC-2131A |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 31A
79 | D00 | AC-2131A-C-02 | 0.4 | GCS-400-NSWG-001A | AC-2131A |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 31A
80 | D00 | AC-2131A-C-03 | 0.4 | GCS-400-NSWG-001A | AC-2131A |  | 10×2.5 | 10C | 2.5 | - | - | 390 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 31A
81 | D00 | AC-2132A-LP-01 | 0.4 | GCS-400-NSWG-001A | AC-2132A | 18.5 | 3×25 | 3C | 25 | - | - | 390 | M32 | M32 | 26.4 | LAL3 | Second Stage Air Cooler 32A
82 | D00 | AC-2132A-C-01 | 0.4 | GCS-400-NSWG-001A | AC-2132A |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 32A
83 | D00 | AC-2132A-C-02 | 0.4 | GCS-400-NSWG-001A | AC-2132A |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 32A
84 | D00 | AC-2132A-C-03 | 0.4 | GCS-400-NSWG-001A | AC-2132A |  | 10×2.5 | 10C | 2.5 | - | - | 390 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 32A
85 | D00 | AC-2131B-LP-01 | 0.4 | GCS-400-NSWG-001B | AC-2131B | 18.5 | 3×35 | 3C | 35 | - | - | 410 | M32 | M32 | 28.6 | LAL3 | Second Stage Air Cooler 31B
86 | D00 | AC-2131B-C-01 | 0.4 | GCS-400-NSWG-001B | AC-2131B |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 31B
87 | D00 | AC-2131B-C-02 | 0.4 | GCS-400-NSWG-001B | AC-2131B |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 31B
88 | D00 | AC-2131B-C-03 | 0.4 | GCS-400-NSWG-001B | AC-2131B |  | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 31B
89 | D00 | AC-2132B-LP-01 | 0.4 | GCS-400-NSWG-001B | AC-2132B | 18.5 | 3×35 | 3C | 35 | - | - | 410 | M32 | M32 | 28.6 | LAL3 | Second Stage Air Cooler 32B
90 | D00 | AC-2132B-C-01 | 0.4 | GCS-400-NSWG-001B | AC-2132B |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 32B
91 | D00 | AC-2132B-C-02 | 0.4 | GCS-400-NSWG-001B | AC-2132B |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 32B
92 | D00 | AC-2132B-C-03 | 0.4 | GCS-400-NSWG-001B | AC-2132B |  | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 32B
93 | D00 | AC-2131C-LP-01 | 0.4 | GCS-400-NSWG-001A | AC-2131C | 18.5 | 3×35 | 3C | 35 | - | - | 410 | M32 | M32 | 28.6 | LAL3 | Second Stage Air Cooler 31C
94 | D00 | AC-2131C-C-01 | 0.4 | GCS-400-NSWG-001A | AC-2131C |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 31C
95 | D00 | AC-2131C-C-02 | 0.4 | GCS-400-NSWG-001A | AC-2131C |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 31C
96 | D00 | AC-2131C-C-03 | 0.4 | GCS-400-NSWG-001A | AC-2131C |  | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 31C
97 | D00 | AC-2132C-LP-01 | 0.4 | GCS-400-NSWG-001A | AC-2132C | 18.5 | 3×35 | 3C | 35 | - | - | 410 | M32 | M32 | 28.6 | LAL3 | Second Stage Air Cooler 32C
98 | D00 | AC-2132C-C-01 | 0.4 | GCS-400-NSWG-001A | AC-2132C |  | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Air Cooler 32C
99 | D00 | AC-2132C-C-02 | 0.4 | GCS-400-NSWG-001A | AC-2132C |  | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Air Cooler 32C
100 | D00 | AC-2132C-C-03 | 0.4 | GCS-400-NSWG-001A | AC-2132C |  | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAL10 | LCS for Air Cooler 32C
101 | D00 | PK-C-2203A-LP-A | 0.4 | GCS-400-NSWG-001A | PK-C-2203A | 40 | 3×240+120 | 4C | 240 | 120 | - | 250 | M90 | M90 | 78.4 | LAN4 | Instrument & Plant Air Package A
102 | D00 | PK-C-2203B-LP-B | 0.4 | GCS-400-NSWG-001B | PK-C-2203B | 40 | 3×240+120 | 4C | 240 | 120 | - | 245 | M90 | M90 | 78.4 | LAN4 | Instrument & Plant Air Package B
103 | D00 | PK-Dr-2203-LP-01 | 0.4 | GCS-400-NSWG-001B | PK-Dr-2203 | 2 | 4×10 | 4C | 10 | 10 | - | 240 | M25 | M25 | 22.1 | LAN4 | Air Dryer Package
104 | D00 | PK-C-2204-LP-01 | 0.4 | GCS-400-NSWG-001A | PK-C-2204 | 30 | 3×185+95 | 4C | 185 | 95 | - | 255 | M75 | M75 | 70.7 | LAN4 | Air Compressor for N2 Package
105 | D00 | PK-2204-LP-01 | 0.4 | GCS-400-NSWG-001A | PK-2204 | 2 | 4×10 | 4C | 10 | 10 | - | 260 | M25 | M25 | 22.1 | LAN4 | Nitrogen Package
106 | D00 | PK-2201-LP-01 | 0.4 | GCS-400-NSWG-001B | PK-2201 | 22.5 | 3×240+120 | 4C | 240 | 120 | - | 520 | M90 | M90 | 78.4 | LAN4 | LP Flare Package
107 | D00 | IG-2201-LP-01 | 0.4 | GCS-400-NSWG-001E | IG-2201 | 2 | 4×6 | 4C | 6 | 6 | - | 210 | M25 | M25 | 24.5 | LAN4 | LP Flare Ignition Package
108 | D00 | IG-2201-LP-02 | 0.4 | IG-2201 | Flare Package | 2 | 4×6 | 4C | 6 | 6 |  | 300 | M25 | M25 | 24.5 | MICC | LP Flare Package
109 | D00 | PK-2207-LP-01 | 0.4 | GCS-400-NSWG-001A | PK-2207 | 2 | 4×10 | 4C | 10 | 10 | - | 270 | M25 | M25 | 22.1 | LAN4 | Corrosion Inhibitor Package
110 | D00 | PK-2208-LP-01 | 0.4 | GCS-400-NSWG-001B | PK-2208 | 2 | 4×10 | 4C | 10 | 10 | - | 270 | M25 | M25 | 22.1 | LAN4 | Methanol Injection Package
111 | D00 | PK-2101-LP-01 | 0.4 | GCS-400-NSWG-001B | PK-2101 | 20 | 3×95+50 | 4C | 95 | 50 | - | 255 | M63 | M63 | 53.8 | LAN4 | Dehydration Package
112 | D00 | P-2203A-LP-A | 0.4 | GCS-400-NSWG-001A | P-2203A | 2.2 | 3×4 | 3C | 4 | - | - | 430 | M20 | M20 | 16.6 | LAL3 | Sump Pump A
113 | D00 | P-2203A-C-01 | 0.4 | GCS-400-NSWG-001A | P-2203A | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Sump Pump A
114 | D00 | P-2203A-C-02 | 0.4 | GCS-400-NSWG-001A | P-2203A | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Sump Pump A
115 | D00 | P-2203A-C-03 | 0.4 | GCS-400-NSWG-001A | P-2203A | - | 10×2.5 | 10C | 2.5 | - | - | 430 | M25 | M25 | 22.9 | CAL10 | LCS for Sump Pump A
116 | D00 | P-2203B-LP-B | 0.4 | GCS-400-NSWG-001B | P-2203B | 2.2 | 3×4 | 3C | 4 | - | - | 430 | M20 | M20 | 16.6 | LAL3 | Sump Pump B
117 | D00 | P-2203B-C-01 | 0.4 | GCS-400-NSWG-001B | P-2203B | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Sump Pump B
118 | D00 | P-2203B-C-02 | 0.4 | GCS-400-NSWG-001B | P-2203B | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Sump Pump B
119 | D00 | P-2203B-C-03 | 0.4 | GCS-400-NSWG-001B | P-2203B | - | 10×2.5 | 10C | 2.5 | - | - | 430 | M25 | M25 | 22.9 | CAL10 | LCS for Sump Pump B
120 | D00 | P-2202A-LP-A | 0.4 | GCS-400-NSWG-001A | P-2202A | 1.1 | 3×4 | 3C | 4 | - | - | 430 | M20 | M20 | 16.6 | LAL3 | Closed Drain Pump A
121 | D00 | P-2202A-C-01 | 0.4 | GCS-400-NSWG-001A | P-2202A | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Closed Drain Pump A
122 | D00 | P-2202A-C-02 | 0.4 | GCS-400-NSWG-001A | P-2202A | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Closed Drain Pump A
123 | D00 | P-2202A-C-03 | 0.4 | GCS-400-NSWG-001A | P-2202A | - | 10×2.5 | 10C | 2.5 | - | - | 430 | M25 | M25 | 22.9 | CAL10 | LCS for Closed Drain Pump A
124 | D00 | P-2202B-LP-B | 0.4 | GCS-400-NSWG-001B | P-2202B | 1.1 | 3×4 | 3C | 4 | - | - | 410 | M20 | M20 | 16.6 | LAL3 | Closed Drain Pump B
125 | D00 | P-2202B-C-01 | 0.4 | GCS-400-NSWG-001B | P-2202B | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Closed Drain Pump B
126 | D00 | P-2202B-C-02 | 0.4 | GCS-400-NSWG-001B | P-2202B | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Closed Drain Pump B
127 | D00 | P-2202B-C-03 | 0.4 | GCS-400-NSWG-001B | P-2202B | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAL10 | LCS for Closed Drain Pump B
128 | D00 | P-2101A-LP-A | 0.4 | GCS-400-NSWG-001A | P-2101A | 30 | 3×35 | 3C | 35 | - | - | 225 | M32 | M32 | 28.6 | LAL3 | Slug Pump A
129 | D00 | P-2101A-C-01 | 0.4 | GCS-400-NSWG-001A | P-2101A | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Slug Pump A
130 | D00 | P-2101A-C-02 | 0.4 | GCS-400-NSWG-001A | P-2101A | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Slug Pump A
131 | D00 | P-2101A-C-03 | 0.4 | GCS-400-NSWG-001A | P-2101A | - | 10×2.5 | 10C | 2.5 | - | - | 225 | M25 | M25 | 22.9 | CAL10 | LCS for Slug Pump A
132 | D00 | P-2101B-LP-B | 0.4 | GCS-400-NSWG-001B | P-2101B | 30 | 3×35 | 3C | 35 | - | - | 225 | M32 | M32 | 28.6 | LAL3 | Slug Pump B
133 | D00 | P-2101B-C-01 | 0.4 | GCS-400-NSWG-001B | P-2101B | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Slug Pump B
134 | D00 | P-2101B-C-02 | 0.4 | GCS-400-NSWG-001B | P-2101B | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Slug Pump B
135 | D00 | P-2101B-C-03 | 0.4 | GCS-400-NSWG-001B | P-2101B | - | 10×2.5 | 10C | 2.5 | - | - | 225 | M25 | M25 | 22.9 | CAL10 | LCS for Slug Pump B
136 | D00 | P-2302A-LP-A | 0.4 | GCS-400-NSWG-001A | P-2302A | 20 | 3×16 | 3C | 16 | - | - | 175 | M25 | M25 | 22.2 | LAN3 | Fire Water Jockey Pump A
137 | D00 | P-2302B-LP-B | 0.4 | GCS-400-NSWG-001B | P-2302B | 20 | 3×16 | 3C | 16 | - | - | 175 | M25 | M25 | 22.2 | LAN3 | Fire Water Jockey Pump B
138 | D00 | P-2209-LP-01 | 0.4 | GCS-400-NSWG-001A | P-2209 | 2.2 | 3×4 | 3C | 4 | - | - | 100 | M20 | M20 | 16.6 | LAN3 | Potable Water Pump
139 | D00 | P-2209-C-01 | 0.4 | GCS-400-NSWG-001A | P-2209 | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAN3 | IRP--ESD for Potable Water Pump
140 | D00 | P-2209-C-02 | 0.4 | GCS-400-NSWG-001A | P-2209 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | IRP--DCS for Potable Water Pump
141 | D00 | P-2209-C-03 | 0.4 | GCS-400-NSWG-001A | P-2209 | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAN10 | LCS for Potable Water Pump
142 | D00 | P-2206-LP-01 | 0.4 | GCS-400-NSWG-001A | P-2206 | 2.2 | 3×4 | 3C | 4 | - | - | 145 | M20 | M20 | 16.6 | LAN3 | Diesel Oil Pump
143 | D00 | P-2206-C-01 | 0.4 | GCS-400-NSWG-001A | P-2206 | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAN3 | IRP--ESD for Diesel Oil Pump
144 | D00 | P-2206-C-02 | 0.4 | GCS-400-NSWG-001A | P-2206 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | IRP--DCS for Diesel Oil Pump
145 | D00 | P-2206-C-03 | 0.4 | GCS-400-NSWG-001A | P-2206 | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAN10 | LCS for Diesel Oil Pump
146 | D00 | P-2201A-LP-A | 0.4 | GCS-400-NSWG-001E | P-2201A | 1.1 | 3×4 | 3C | 4 | - | - | 430 | M20 | M20 | 16.6 | LAN3 | LP Flare K.O. Drum Pump A
147 | D00 | P-2201A-C-01 | 0.4 | GCS-400-NSWG-001E | P-2201A | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAN3 | IRP--ESD for LP Flare K.O. Drum Pump A
148 | D00 | P-2201A-C-02 | 0.4 | GCS-400-NSWG-001E | P-2201A | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | IRP--DCS for LP Flare K.O. Drum Pump A
149 | D00 | P-2201A-C-03 | 0.4 | GCS-400-NSWG-001E | P-2201A | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAN10 | LCS for LP Flare K.O. Drum Pump A
150 | D00 | P-2201B-LP-B | 0.4 | GCS-400-NSWG-001E | P-2201B | 1.1 | 3×4 | 3C | 4 | - | - | 430 | M20 | M20 | 16.6 | LAN3 | LP Flare K.O. Drum Pump B
151 | D00 | P-2201B-C-01 | 0.4 | GCS-400-NSWG-001E | P-2201B | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAN3 | IRP--ESD for LP Flare K.O. Drum Pump B
152 | D00 | P-2201B-C-02 | 0.4 | GCS-400-NSWG-001E | P-2201B | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAN12 | IRP--DCS for LP Flare K.O. Drum Pump B
153 | D00 | P-2201B-C-03 | 0.4 | GCS-400-NSWG-001E | P-2201B | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAN10 | LCS for LP Flare K.O. Drum Pump B
154 | D00 | P-2103A-LP-A | 0.4 | GCS-400-NSWG-001A | P-2103A | 1.5 | 3×4 | 3C | 4 | - | - | 360 | M20 | M20 | 16.6 | LAL3 | Glycol Transfer Pump A
155 | D00 | P-2103A-C-01 | 0.4 | GCS-400-NSWG-001A | P-2103A | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Glycol Transfer Pump A
156 | D00 | P-2103A-C-02 | 0.4 | GCS-400-NSWG-001A | P-2103A | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Glycol Transfer Pump A
157 | D00 | P-2103A-C-03 | 0.4 | GCS-400-NSWG-001A | P-2103A | - | 10×2.5 | 10C | 2.5 | - | - | 410 | M25 | M25 | 22.9 | CAL10 | LCS for Glycol Transfer Pump A
158 | D00 | P-2103B-LP-B | 0.4 | GCS-400-NSWG-001B | P-2103B | 1.5 | 3×4 | 3C | 4 | - | - | 360 | M20 | M20 | 16.6 | LAL3 | Glycol Transfer Pump B
159 | D00 | P-2103B-C-01 | 0.4 | GCS-400-NSWG-001B | P-2103B | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Glycol Transfer Pump B
160 | D00 | P-2103B-C-02 | 0.4 | GCS-400-NSWG-001B | P-2103B | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Glycol Transfer Pump B
161 | D00 | P-2103B-C-03 | 0.4 | GCS-400-NSWG-001B | P-2103B | - | 10×2.5 | 10C | 2.5 | - | - | 360 | M25 | M25 | 22.9 | CAL10 | LCS for Glycol Transfer Pump B
162 | D00 | P-2102-LP-01 | 0.4 | GCS-400-NSWG-001B | P-2102 | 1.1 | 3×4 | 3C | 4 | - | - | 360 | M20 | M20 | 16.6 | LAL3 | Glycol Manual Pump
163 | D00 | P-2104-LP-01 | 0.4 | GCS-400-NSWG-001B | P-2104 | 1.1 | 3×4 | 3C | 4 | - | - | 430 | M20 | M20 | 16.6 | LAL3 | Glycol Drain Pump
164 | D00 | P-2104-C-01 | 0.4 | GCS-400-NSWG-001B | P-2104 | - | 3×2.5 | 3C | 2.5 | - | - | 50 | M20 | M20 | 15.3 | CAL3 | IRP--ESD for Glycol Drain Pump
165 | D00 | P-2104-C-02 | 0.4 | GCS-400-NSWG-001B | P-2104 | - | 12×2.5 | 12C | 2.5 | - | - | 50 | M25 | M25 | 23.5 | CAL12 | IRP--DCS for Glycol Drain Pump
166 | D00 | P-2104-C-03 | 0.4 | GCS-400-NSWG-001B | P-2104 | - | 10×2.5 | 10C | 2.5 | - | - | 430 | M25 | M25 | 22.9 | CAL10 | LCS for Glycol Drain Pump
167 | D00 | CR-01-LP-01 | 0.4 | GCS-400-NSWG-001A | GCS-400-CR-01 | 10 | 3×70+35 | 4C | 70 | 35 | - | 335 | M50 | M50 | 47.9 | LAL4 | Main Compressor Crane
168 | D00 | CR-02-LP-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-CR-02 | 5 | 4×16 | 4C | 16 | 16 | - | 175 | M25 | M25 | 24.5 | LAN4 | Fire Water Pumps Crane
169 | D00 | NDB-01-LP-01 | 0.4 | GCS-400-NSWG-001A | GCS-400-NDB-01 | 20 | 3×150+70 | 4C | 150 | 70 | - | 330 | M63 | M63 | 64.8 | LAL4 | Process Area Normal Lighting Panel
170 | D00 | EDB-01-LP-01 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDB-01 | 10 | 3×70+35 | 4C | 70 | 35 | - | 330 | M50 | M50 | 47.9 | LAL4 | Process Area Emergency Lighting Panel
171 | D00 | NDB-02-LP-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-NDB-02 | 10 | 4×35 | 4C | 35 | 35 | - | 180 | M32 | M32 | 32.1 | LAN4 | Utility Area Normal Lighting Panel
172 | D00 | EDB-02-LP-01 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDB-02 | 5 | 4×16 | 4C | 16 | 16 | - | 180 | M25 | M25 | 24.5 | LAN4 | Utility Area Emergency Lighting Panel
173 | D00 | WS-01-LP-01 | 0.4 | GCS-400-NSWG-001A | GCS-400-WS-01 | 37 | 3×2×120+70 | 4C | 120 | 70 | - | 350 | M63 | M63 | 59.3 | LAL4 | Welding Receptacle (3 Phase) (Process Area)
174 | D00 | WS-02-LP-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-WS-02 | 37 | 3×150+70 | 4C | 150 | 70 | - | 200 | M63 | M63 | 64.8 | LAN4 | Welding Receptacle (3 Phase) (Utility Area)
175 | D00 | CP01-LP-01 | 0.4 | GCS-400-NSWG-001A | GCS-400-CP01 | 5 | 4×16 | 4C | 16 | 16 | - | 150 | M25 | M25 | 24.5 | LAN4 | Cathodic Protection Transformer Rectifier1
176 | D00 | CP02-LP-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-CP02 | 10 | 4×25 | 4C | 25 | 25 | - | 150 | M32 | M32 | 28.4 | LAN4 | Cathodic Protection Transformer Rectifier2
177 | D00 | HVAC-LP-01 | 0.4 | GCS-400-NSWG-001E | CTRL- HVAC | 150 | 3×2×150+70 | 4C | 150 | 120 | - | 50 | M63 | M63 | 64.8 | LAN4 | HVAC Panel for Control Room
178 | D00 | CHG-001-LP-A1 | 0.4 | GCS-400-NSWG-001A | GCS-110-CHG-001 | 20 | 4×16 | 4C | 16 | 16 | - | 50 | M25 | M25 | 24.5 | LAN4 | 110VDC Charger 1
179 | D00 | FB1-LP-A1 | 0.11DC | GCS-110-CHG-001 | Fuse Box 1 | - | 2×16 | 2C | 16 | - | - | 20 | M25 | M25 | 21.2 | LAN2 | DC Charger Fuse Box 1
180 | D00 | BAT1-LP-A1 | 0.11DC | Fuse Box 1 | Battery Bank 1 | - | 2×16 | 2C | 16 | - | - | 20 | M25 | M25 | 21.2 | LAN2 | DC Charger Battery Bank 1
181 | D00 | CHG-002-LP-A2 | 0.4 | GCS-400-NSWG-001E | GCS-110-CHG-002 | 20 | 4×16 | 4C | 16 | 16 | - | 50 | M25 | M25 | 24.5 | LAN4 | 110VDC Charger 2
182 | D00 | FB2-LP-A2 | 0.11DC | GCS-110-CHG-002 | Fuse Box 2 | - | 2×16 | 2C | 16 | - | - | 10 | M25 | M25 | 21.2 | LAN2 | DC Charger Fuse Box 2
183 | D00 | BAT2-LP-A2 | 0.11DC | Fuse Box 2 | Battery Bank 2 | - | 2×16 | 2C | 16 | - | - | 10 | M25 | M25 | 21.2 | LAN2 | DC Charger Battery Bank 2
184 | D00 | CHG-002-LP-A3 | 0.4 | GCS-400-NSWG-001A | GCS-24-CHG-001 | 13 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | 24VDC Charger 1
185 | D00 | FB1-LP-A3 | 0.24DC | GCS-110-CHG-001 | Fuse Box 1 | - | 2×10 | 2C | 10 | - | - | 10 | M25 | M25 | 19.8 | LAN2 | DC Charger Fuse Box 1
186 | D00 | BAT2-LP-A3 | 0.24DC | Fuse Box 1 | Battery Bank 1 | - | 2×10 | 2C | 10 | - | - | 10 | M25 | M25 | 19.8 | LAN2 | DC Charger Battery Bank 1
187 | D00 | CHG-002-LP-A4 | 0.4 | GCS-400-NSWG-001E | GCS-24-CHG-002 | 13 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | 24VDC Charger 2
188 | D00 | FB2-LP-A4 | 0.24DC | GCS-24-CHG-002 | Fuse Box 2 | - | 2×10 | 2C | 10 | - | - | 10 | M25 | M25 | 19.8 | LAN2 | DC Charger Fuse Box 2
189 | D00 | BAT2-LP-A4 | 0.24DC | Fuse Box 2 | Battery Bank 2 | - | 2×10 | 2C | 10 | - | - | 10 | M25 | M25 | 19.8 | LAN2 | DC Charger Battery Bank 2
190 | D00 | UPS-001-LP-A5 | 0.4 | GCS-400-NSWG-001A | GCS-110-UPS-001 | 49 | 3×70+35 | 4C | 70 | 35 | - | 50 | M50 | M50 | 47.9 | LAN4 | 110VAC UPS 1
191 | D00 | FB1-LP-A5 | 0.11AC | GCS-110-UPS-001 | Fuse Box 1 | - | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | LAN2 | UPS Fuse Box 1
192 | D00 | BAT2-LP-A5 | 0.11AC | Fuse Box 1 | Battery Bank 1 | - | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | LAN2 | UPS Battery Bank 1
193 | D00 | UPS-002-LP-A6 | 0.4 | GCS-400-NSWG-001E | GCS-110-UPS-002 | 49 | 3×70+35 | 4C | 70 | 35 | - | 50 | M50 | M50 | 47.9 | LAN4 | 110VAC UPS 2
194 | D00 | FB2-LP-A6 | 0.11AC | GCS-110-UPS-002 | Fuse Box 2 | - | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | LAN2 | UPS Fuse Box 2
195 | D00 | BAT2-LP-A6 | 0.11AC | Fuse Box 2 | Battery Bank 2 | - | 2×50 | 2C | 50 | - | - | 20 | M32 | M32 | 30.2 | LAN2 | UPS Battery Bank 2
196 | D00 | UPS-Bypass-LP-01 | 0.4 | GCS-400-NSWG-001E | GCS-110-UPS-Bypass | 20 | 4×10 | 4C | 10 | 10 | - | 50 | M25 | M25 | 22.1 | LAN4 | 110VAC UPS By Pass
197 | D00 | Non UPS-LP-01 | 0.4 | GCS-400-NSWG-001E | GCS-400-Non UPS | 8 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | Non-UPS Load for Instrument
198 | D00 | NDB-CAP--LP-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-NDB-CAP | 5 | 4×4 | 4C | 4 | 4 | - | 20 | M20 | M20 | 17.7 | LAN4 | Capacitor Room Normal Lighting Panel
199 | D00 | MOV 1-LP-01 | 0.4 | GCS-400-NSWG-001A |  | 2 | 4×6 | 4C | 6 | 6 | - | 175 | M25 | M25 | 19.7 | LAN4 | MOV 1
200 | D00 | FDP 01-LP-01 | 0.4 | GCS-400-NSWG-001E | GCS-230-FDP 01 | 2 | 4×6 | 4C | 6 | 6 | - | 175 | M25 | M25 | 19.7 | LAN4 | Fire Diesel Panel 01
201 | D00 | FDP 02-LP-02 | 0.4 | GCS-400-NSWG-001E | GCS-230-FDP 02 | 2 | 4×6 | 4C | 6 | 6 | - | 175 | M25 | M25 | 19.7 | LAN4 | Fire Diesel Panel 02
202 | D00 | SPH-01-LP-01 | 0.4 | GCS-400-NSWG-001E | SPH-01 | 2 | 4×4 | 4C | 4 | 4 | - | 30 | M20 | M20 | 17.7 | LAN4 | Space Heater & Lighting for New LV Switchgear
203 | D00 | SPH-02-LP-01 | 0.4 | GCS-400-NSWG-001E | SPH-02 | 2 | 4×4 | 4C | 4 | 4 | - | 30 | M20 | M20 | 17.7 | LAN4 | Space Heater & Lighting for MV Switchgear
204 | D00 | NDP-CRM-LP-01 | 0.4 | GCS-400-NSWG-001B | GCS-400-NDP-CRM | 30 | 4×25 | 4C | 25 | 25 | - | 50 | M32 | M32 | 28.4 | LAN4 | Control Room Normal Lighting Panel
205 | D00 | EDP-CRM-LP-01 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDP-CRM | 15 | 4×16 | 4C | 16 | 16 | - | 50 | M25 | M25 | 24.5 | LAN4 | Control Room Emergency Lighting Panel
206 | D00 | EDB-CAP-LP-01 | 0.4 | GCS-400-NSWG-001E | GCS-400-EDB-CAP | 5 | 4×4 | 4C | 4 | 4 | - | 20 | M20 | M20 | 17.7 | LAN4 | Capacitor Room Emergency Lighting Panel
207 | D00 | LV-HVAC01-LP-01 | 0.4 | GCS-400-NSWG-001A | LV-HVAC01 | 7 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | Split Feeder (HVAC Feeder-01 for LV Room)
208 | D00 | LV-HVAC02-LP-02 | 0.4 | GCS-400-NSWG-001B | LV-HVAC02 | 7 | 4×6 | 4C | 6 | 6 | - | 50 | M25 | M25 | 19.7 | LAN4 | Split Feeder (HVAC Feeder-02 for LV Room)
209 | D00 | MV-HVAC01-LP-01 | 0.4 | GCS-400-NSWG-001A | MV-HVAC01 | 7 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN4 | Split Feeder (HVAC Feeder-01 for MV Room)
210 | D00 | MV-HVAC02-LP-01 | 0.4 | GCS-400-NSWG-001B | MV-HVAC02 | 7 | 4×4 | 4C | 4 | 4 | - | 10 | M20 | M20 | 17.7 | LAN4 | Split Feeder (HVAC Feeder-02 for MV Room)
211 | D00 | HVAC01-LP-01 | 0.4 | GCS-400-NSWG-001A | CAP-HVAC01 | 5 | 4×4 | 4C | 4 | 4 | - | 20 | M20 | M20 | 17.7 | LAN4 | Split Feeder (HVAC Feeder-01 for Capacitor Room)
212 | D00 | HVAC02-LP-02 | 0.4 | GCS-400-NSWG-001B | CAP-HVAC02 | 5 | 4×4 | 4C | 4 | 4 | - | 20 | M20 | M20 | 17.7 | LAN4 | Split Feeder (HVAC Feeder-02 for Capacitor Room)
213 | D00 | CAP-01-LP-01A | 0.4 | GCS-400-NSWG-001A | CAP-01 | 100 | 3×120 | 3C | 120 |  |  | 20 | M50 | M50 | 45.8 | LN3 | Capacitor Bank 1
214 | D00 | CAP-01-LP-01B | 0.4 | GCS-400-NSWG-001A | CAP-01 | 100 | 3×120 | 3C | 120 |  |  | 20 | M50 | M50 | 45.8 | LN3 | Capacitor Bank 1
215 | D00 | CAP-02-LP-02A | 0.4 | GCS-400-NSWG-001B | CAP-02 | 100 | 3×120 | 3C | 120 |  |  | 20 | M50 | M50 | 45.8 | LN3 | Capacitor Bank 2
216 | D00 | CAP-02-LP-02B | 0.4 | GCS-400-NSWG-001B | CAP-02 | 100 | 3×120 | 3C | 120 |  |  | 20 | M50 | M50 | 45.8 | LN3 | Capacitor Bank 2