## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 12
9184 – 073 - 053 |  |  | BK |  | SSGRL | PEDCO | 110 |  | IN | DT | 0001 | D03
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR WHCP/HPU - WELLHEADS نگهداشت و افزایش تولید میدان نفتی بینک
D03 |  | JUN.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D02 |  | DEC.2021 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | NOV.2021 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | AUG.2021 |  | IFC |  |  |  | M.Asgharnejad |  |  | M.Fakharian |  | Sh.Ghalikar
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-707368
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 12
9184 – 073 - 053 |  |  | BK | SSGRL |  | PEDCO | 000 | IN | DT | 0001 |  | D03
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X |  | X |  |  |  | 65
2 | X | X | X |  | X |  |  |  | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X |  | X |  | X |  |  |  | 70
7 | X |  | X | [5 empty] | 71
8 | X |  | X |  | X |  |  |  | 72
9 |  |  | X |  | X |  |  |  | 73
10 |  |  | X |  | X |  |  |  | 74
11 |  |  | X | [5 empty] | 75
12 |  |  | X |  | X |  |  |  | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 3 از 12
9184 – 073 - 053 |  |  | BK | SSGRL | PEDCO | 000 | IN | DT | 0001 | D03
REFERENCE DOCUMENTS:
1- SPECIFICATION FOR INSTRUMENTATION | [10 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001
2- PIPING AND PIPELINE MATERIAL SPECIFICATION | [10 empty] | BK-SSGRL-PEDCO-110-PI-SP-0001
3- PIPING & INSTRUMENT DIAGRAM:
|  | P&ID - W018S | [8 empty] | BK-W018S-PEDCO-110-PR-PI-0001
|  | P&ID - W028 | [8 empty] | BK-W028-PEDCO-110-PR-PI-0001
|  | P&ID - W035 | [8 empty] | BK-W035-PEDCO-110-PR-PI-0001
|  | P&ID - W008N | [8 empty] | BK-W008N-PEDCO-110-PR-PI-0001
4- SPECIFICATION FOR WHCP/HPU | [10 empty] | BK-SSGRL-PEDCO-110-IN-SP-0001
| 5- WHCP HYDRAULIC/PNEUMATIC DIAGRAM- WELLHEADS | [9 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
| 6- INSTRUMENT & CONTROL DESIGN CRITERIA | [9 empty] | BK-SSGRL-PEDCO-110-IN-DC-0002
D03

## Note 1
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 12
9184 – 073 - 053 |  | BK | SSGRL | PEDCO | 000 | IN | DT | 0001 | D03
GENERAL NOTES
1- Environmental Condition For Field Instrumentation Of Binak wellhead area Shall Be Considered | [10 empty] | ENVIRONMENTAL CONDITION FOR FIELD INSTRUMENTATION OF BINAK COMPLEX SHALL BE CONSIDERED AS PER THE FOLLOWING:
as Per The Following:
| • Minimum ambient temperature (°C): -5 °C • Maximum ambient temperature (°C): 50 °C • Maximum steel surface exposed to sun (°C): 85 °C | [10 empty] | 3 ºC
| Relative Humidity: | [10 empty] | 49 ºC
| • Maximum Design relative humidity: 100% • Minimum Design relative humidity: 0% | [10 empty] | 55 ºC
-5 ºC
46.5 ºC
100%@25.6 OC
2% @49.6 OC
13%
D03

## 018S
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | SSGRL |  | PEDCO |  | 000 |  | IN | DT |  | 0001 | D03
WELLHEAD CONTROL PANEL FOR WELL NO. W018S
GENERAL DATA |  |  | 1 | TAG NUMBERS | [7 empty] | WHCP-1101
|  |  | 2 | DIMENSIONS FOR PANEL | [7 empty] | VTA
|  |  | 3 | P&ID NO. | [7 empty] | BK-W018S-PEDCO-110-PR-PI-0001
|  |  | 4 | HYDRAULIC DIAGRAM NO. | [7 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
|  |  | 5 | NUMBER OF WELLS PER WHCP /NUMBER OF ATUMATIC VALVES PER WELL | [7 empty] | 1 WELL/2 VALVE(SSV/SSSV)
SITE CONDITION |  |  | 6 | AS PER PROJECT REQUIREMENT | [7 empty] | REFER TO NOTE 1 IN PAGE 4(GENERAL NOTES)
PROCESS DATA |  |  | 7 | WELL DESIGN PRESSURE(PSI) | [7 empty] | 5000
|  |  | 8 | WELL OPERATING PRESSURE(PSI) | [7 empty] | 650
|  |  | 9 | WELL DESIGN TEMPERATURE(ᵒC) | [7 empty] | 100
|  |  | 10 | WELL OPERATING TEMPERATURE(ᵒC) | [7 empty] | 75
SSV/SSSV SPECIFICATION DATA |  |  | 11 | SSV SWEPT VOLUME/ CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 5 LITER/3000 PSI(NOTE 5)
|  |  | 12 | SSSV SWEPT VOLUME / CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 2.5 LITER/5000 PSI(NOTE 5)
|  |  | 13 | SSV OPEN& CLOSE TIME /SSSV OPEN&CLOSE TIME | [7 empty] | 2/8 (NOTE 5)
|  |  | 14 | SSV / SSSV CONNECTION SIZE | [7 empty] | 1/2" / 1/4"(NOTE 5)
WHCP ENCLOSURE |  |  | 15 | IP RATING | [7 empty] | IP 65(NOTE 1)
|  |  | 16 | NACE MR0175/ISO 15156 COMPLIANCE | [7 empty] | NOT REQUIRED EXCEPT FOR PSHH/ PSLL AS PER BELOW TABLE
|  |  | 17 | NAME PLATE | [7 empty] | BOTH TAG AND WELL NUMBER TO BE INCLUDED IN NAME PLATE
|  |  | 18 | MATERIAL OF WHCP AND ALL ACCESSORIES | [7 empty] | 316 SS (NOTE 1)
|  |  | 19 | PANEL ACCESSORIES | [7 empty] | AS MINIMUM AS PER PROJECT (NOTE 1,5)
HPU |  |  | 20 | NUMBER OF OIL TANK/ VOLUME FOR OIL TANK | [7 empty] | 2 TANKS /ONE AS THE MAIN OIL TANK AND ONE FOR SSSV RETURN LINE (NOTE 9)
|  |  | 21 | NUMBER OF ACCUMULATOR | [7 empty] | 2 NO. FOR HP/MP HEADERS (VTC)
|  |  | 22 | PUMP REQUIREMENT | [7 empty] | N2 DRIVEN AND HAND PUMPS(NOTE 1,3)
|  |  | 23 | PUMP MAX. WORKING PRESSURE | [7 empty] | 5000 PSI (EACH PUMPS SEPARATELY)
NITROGEN BOTTLES/ PNEUMATIC SUPPLY (PER PANEL) (NOTE 1,2) |  |  | 24 | NUMBER OF BOTTLES | [7 empty] | VENDOR TO ADVISE (CALCULATION TO BE PROVIDED)(NOTE 2)
|  |  | 25 | DIMENSIONS FOR BOTTLES RACK | [7 empty] | VENDOR TO ADVISE(NOTE 2)
|  |  | 26 | PRESSURE GAUGES FOR EACH HEADER | [7 empty] | REQUIRED(NOTE 1)
PANEL MOUNTED GAUGES |  |  | 27 | PRESSURE GAUGES ON PANEL FRONT | [7 empty] | FRONT FACE MOUNTED, AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
|  |  | 28 | PRESSURE GAUGES MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 29 | DIAL SIZE | [7 empty] | 60 mm
SSV/SSSV COMMAND TUBING(NOTE 8,9) |  |  | 30 | TUBE SIZE TO SSV/ SSSV(BY WHCP VENDOR) | [7 empty] | 1/2" / 1/4"(NOTE 5)
|  |  | 31 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 32 | TUBE LENGTH FROM WELL TO SSV/ SSSV (BY WHCP VENDOR) | [7 empty] | 30 m /30 m
FUSIBLE PLUG LOOP (NOTE 8,9) |  |  | 33 | TUBE SIZE | [7 empty] | 1/4"
|  |  | 34 | TUBE LENGTH TO AROUND WELL (BY WHCP VENDOR) | [7 empty] | 50m
|  |  | 35 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 36 | NUMBER OF FUSIBLE PLUG FOR EACH WELL/SET POINT | [7 empty] | 3 NO. (SET POINT:100ᵒC)
PANEL MOUNTED PUSH BUTTONS |  |  | 37 | ESD RESSET FUNCTION/SSV AND SSSV OPEN/CLOSE COMMAND FOR EACH WELL | [7 empty] | REQUIRED DEDICATED FRONT FACE PUSH BUTTONS AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
PANEL MOUNTED INDICATORS/ LAMPS |  |  | 38 | VALVES OPEN & CLOSE FEEDBACK STATUS | [7 empty] | REQUIRED DEDICATED FRONT FACE INDICATORS AS PER PROJECT DIAGRAMS(VTC)(NOTE 6,1)
PRESSURE PILOT |  |  | 39 | PRESSURE SWITCHES FOR PRESSURE SENSING LINE | [7 empty] | 4 NO. FOR EACH PANEL
SPARE PART |  |  | 40 | SPARE PARTS FOR COMMISSIONING AND START-UP | [7 empty] | REQUIRED(NOTE 1)
|  |  | 41 | SPARE PARTS FOR TWO YEARS OPERATION | [7 empty] | REQUIRED(NOTE 1)
INSPECTION & TEST |  |  | 42 | AS PER PROJECT REQUIREMENT | [7 empty] | REQUIRED(NOTE 1)
PURCHASE |  |  | 43 | MANUFACTURER | [7 empty] | FINALIZED BASED ON VENDOR DATA
|  |  | 44 | MODEL | [7 empty] | FINALIZED BASED ON VENDOR DATA
RELATED DATA SHEETS FOR PRESSURE SENSING LINE AND SWITCHES
TAG NO. | PSHH-1101A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 2500
TAG NO. | PSLL-1101A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 194.575
TAG NO. | PSHH-1101B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 202.71
TAG NO. | PSLL-1101B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W018S-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1101 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 176.044
NOTE:
VTA : VENDOR TO ADVISE |  |  | VTC: VENDOR TO CONFIRM |  |  |  |  | NIA: NOT APPLICABLE
1- FOR DETAIL DATA REFER TO DOC.:SPECIFICATION FOR WHCP/HPU, BK-SSGRL-PEDCO-110-IN-SP-0001.
2- AS MINIMUM, BOTTLES WITH CAPACITY OF 50 LITER WITH QUANTITY: 4 MAIN BOTTLES AND 4 RESERVED BOTTLES SHALL BE CONSIDERED
3- NITROGEN GAS FOR N2 DRIVEN PUMP SUPPLY AT LEAST FOR TWO TIMES ACTUATION OF EACH VALVES (SSV AND SSSV) IS REQUIRED.
4- THE WHCP PANEL SHALL BE SUPPLIED WITH “FIRST OUT” FEATURE SO THE PANEL LOGIC SHALL BE DESIGNED IN A MANNER THAT FIRST CAUSE OF PANEL
SHUTDOWN BE DISTINGUISHABLE FOR MAINTENANCE PURPOSES.
5- TO BE FINALIZED BASED ON SSV/SSSV VENDOR FINAL DATA BOOK.
6- REFER TO "WHCP HYDRAULIC DIAGRAM,BK-SSGRL-PEDCO-110-IN-DG-0002".
7- ALL TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE SUPPLIED BY WHCP VENDOR
8- THE QUANTITY OF TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE FINALIZED BY WHCP VENDOR.
9- THE MINIMUM VOLUME OF OIL TANK(50 LITER) SHALL BE CONSIDERED IN ACCORDANCE TO THE CAPACITY OF SSV/SSSV AND THE HYDRAULIC OIL
LINE.
D03

## 008N
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | SSGRL |  | PEDCO |  | 000 |  | IN | DT |  | 0001 | D03
WELLHEAD CONTROL PANEL FOR WELL NO. W008N
GENERAL DATA |  |  | 1 | TAG NUMBERS | [7 empty] | WHCP-1601
|  |  | 2 | DIMENSIONS FOR PANEL | [7 empty] | VTA
|  |  | 3 | P&ID NO. | [7 empty] | BK-W008N-PEDCO-110-PR-PI-0001
|  |  | 4 | HYDRAULIC DIAGRAM NO. | [7 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
|  |  | 5 | NUMBER OF WELLS PER WHCP /NUMBER OF ATUMATIC VALVES PER WELL | [7 empty] | 1 WELL/2 VALVE(SSV/SSSV)
SITE CONDITION |  |  | 6 | AS PER PROJECT REQUIREMENT | [7 empty] | REFER TO NOTE 1 IN PAGE 4(GENERAL NOTES)
PROCESS DATA |  |  | 7 | WELL DESIGN PRESSURE(PSI) | [7 empty] | 5000
|  |  | 8 | WELL OPERATING PRESSURE(PSI) | [7 empty] | 650
|  |  | 9 | WELL DESIGN TEMPERATURE(ᵒC) | [7 empty] | 100
|  |  | 10 | WELL OPERATING TEMPERATURE(ᵒC) | [7 empty] | 75
SSV/SSSV SPECIFICATION DATA |  |  | 11 | SSV SWEPT VOLUME/ CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 5 LITER/3000 PSI(NOTE 5)
|  |  | 12 | SSSV SWEPT VOLUME / CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 2.5 LITER/5000 PSI(NOTE 5)
|  |  | 13 | SSV OPEN& CLOSE TIME /SSSV OPEN&CLOSE TIME | [7 empty] | 2/8 (NOTE 5)
|  |  | 14 | SSV / SSSV CONNECTION SIZE | [7 empty] | 1/2" / 1/4"(NOTE 5)
WHCP ENCLOSURE |  |  | 15 | IP RATING | [7 empty] | IP 65(NOTE 1)
|  |  | 16 | NACE MR0175/ISO 15156 COMPLIANCE | [7 empty] | NOT REQUIRED EXCEPT FOR PSHH/ PSLL AS PER BELOW TABLE
|  |  | 17 | NAME PLATE | [7 empty] | BOTH TAG AND WELL NUMBER TO BE INCLUDED IN NAME PLATE
|  |  | 18 | MATERIAL OF WHCP AND ALL ACCESSORIES | [7 empty] | 316 SS (NOTE 1)
|  |  | 19 | PANEL ACCESSORIES | [7 empty] | AS MINIMUM AS PER PROJECT (NOTE 1,5)
HPU |  |  | 20 | NUMBER OF OIL TANK/ VOLUME FOR OIL TANK | [7 empty] | 2 TANKS /ONE AS THE MAIN OIL TANK AND ONE FOR SSSV RETURN LINE (NOTE 9)
|  |  | 21 | NUMBER OF ACCUMULATOR | [7 empty] | 2 NO. FOR HP/MP HEADERS (VTC)
|  |  | 22 | PUMP REQUIREMENT | [7 empty] | N2 DRIVEN AND HAND PUMPS(NOTE 1,3)
|  |  | 23 | PUMP MAX. WORKING PRESSURE | [7 empty] | 5000 PSI (EACH PUMPS SEPARATELY)
NITROGEN BOTTLES/ PNEUMATIC SUPPLY (PER PANEL) (NOTE 1,2) |  |  | 24 | NUMBER OF BOTTLES | [7 empty] | VENDOR TO ADVISE (CALCULATION TO BE PROVIDED)(NOTE 2)
|  |  | 25 | DIMENSIONS FOR BOTTLES RACK | [7 empty] | VENDOR TO ADVISE(NOTE 2)
|  |  | 26 | PRESSURE GAUGES FOR EACH HEADER | [7 empty] | REQUIRED(NOTE 1)
PANEL MOUNTED GAUGES |  |  | 27 | PRESSURE GAUGES ON PANEL FRONT | [7 empty] | FRONT FACE MOUNTED, AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
|  |  | 28 | PRESSURE GAUGES MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 29 | DIAL SIZE | [7 empty] | 60 mm
SSV/SSSV COMMAND TUBING(NOTE 8,9) |  |  | 30 | TUBE SIZE TO SSV/ SSSV(BY WHCP VENDOR) | [7 empty] | 1/2" / 1/4"(NOTE 5)
|  |  | 31 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 32 | TUBE LENGTH FROM WELL TO SSV/ SSSV (BY WHCP VENDOR) | [7 empty] | 30 m /30 m
FUSIBLE PLUG LOOP (NOTE 8,9) |  |  | 33 | TUBE SIZE | [7 empty] | 1/4"
|  |  | 34 | TUBE LENGTH TO AROUND WELL (BY WHCP VENDOR) | [7 empty] | 50m
|  |  | 35 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 36 | NUMBER OF FUSIBLE PLUG FOR EACH WELL/SET POINT | [7 empty] | 3 NO. (SET POINT:100ᵒC)
PANEL MOUNTED PUSH BUTTONS |  |  | 37 | ESD RESSET FUNCTION/SSV AND SSSV OPEN/CLOSE COMMAND FOR EACH WELL | [7 empty] | REQUIRED DEDICATED FRONT FACE PUSH BUTTONS AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
PANEL MOUNTED INDICATORS/ LAMPS |  |  | 38 | VALVES OPEN & CLOSE FEEDBACK STATUS | [7 empty] | REQUIRED DEDICATED FRONT FACE INDICATORS AS PER PROJECT DIAGRAMS(VTC)(NOTE 6,1)
PRESSURE PILOT |  |  | 39 | PRESSURE SWITCHES FOR PRESSURE SENSING LINE | [7 empty] | 4 NO. FOR EACH PANEL
SPARE PART |  |  | 40 | SPARE PARTS FOR COMMISSIONING AND START-UP | [7 empty] | REQUIRED(NOTE 1)
|  |  | 41 | SPARE PARTS FOR TWO YEARS OPERATION | [7 empty] | REQUIRED(NOTE 1)
INSPECTION & TEST |  |  | 42 | AS PER PROJECT REQUIREMENT | [7 empty] | REQUIRED(NOTE 1)
PURCHASE |  |  | 43 | MANUFACTURER | [7 empty] | FINALIZED BASED ON VENDOR DATA
|  |  | 44 | MODEL | [7 empty] | FINALIZED BASED ON VENDOR DATA
RELATED DATA SHEETS FOR PRESSURE SENSING LINE AND SWITCHES
TAG NO. | PSHH-1601A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 2500
TAG NO. | PSLL-1601A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 194.575
TAG NO. | PSHH-1601B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 202.71
TAG NO. | PSLL-1601B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W008N-PEDCO-110-PR-PI-0001 |  |  |  | 75 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1601 |  |  |  | 100 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 176.044
NOTE:
VTA : VENDOR TO ADVISE |  |  | VTC: VENDOR TO CONFIRM |  |  |  |  | NIA: NOT APPLICABLE
1- FOR DETAIL DATA REFER TO DOC.:SPECIFICATION FOR WHCP/HPU, BK-SSGRL-PEDCO-110-IN-SP-0001.
2- AS MINIMUM, BOTTLES WITH CAPACITY OF 50 LITER WITH QUANTITY: 4 MAIN BOTTLES AND 4 RESERVED BOTTLES SHALL BE CONSIDERED
3- NITROGEN GAS FOR N2 DRIVEN PUMP SUPPLY AT LEAST FOR TWO TIMES ACTUATION OF EACH VALVES (SSV AND SSSV) IS REQUIRED.
4- THE WHCP PANEL SHALL BE SUPPLIED WITH “FIRST OUT” FEATURE SO THE PANEL LOGIC SHALL BE DESIGNED IN A MANNER THAT FIRST CAUSE OF PANEL
SHUTDOWN BE DISTINGUISHABLE FOR MAINTENANCE PURPOSES.
5- TO BE FINALIZED BASED ON SSV/SSSV VENDOR FINAL DATA BOOK.
6- REFER TO "WHCP HYDRAULIC DIAGRAM,BK-SSGRL-PEDCO-110-IN-DG-0002".
7- ALL TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE SUPPLIED BY WHCP VENDOR
8- THE QUANTITY OF TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE FINALIZED BY WHCP VENDOR.
9- THE MINIMUM VOLUME OF OIL TANK(50 LITER) SHALL BE CONSIDERED IN ACCORDANCE TO THE CAPACITY OF SSV/SSSV AND THE HYDRAULIC OIL
LINE.
D03

## 028
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | SSGRL |  | PEDCO |  | 000 |  | IN | DT |  | 0001 | D03
WELLHEAD CONTROL PANEL FOR WELL NO. W028
GENERAL DATA |  |  | 1 | TAG NUMBERS | [7 empty] | WHCP-1401
|  |  | 2 | DIMENSIONS FOR PANEL | [7 empty] | VTA
|  |  | 3 | P&ID NO. | [7 empty] | BK-W028-PEDCO-110-PR-PI-0001
|  |  | 4 | HYDRAULIC DIAGRAM NO. | [7 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
|  |  | 5 | NUMBER OF WELLS PER WHCP /NUMBER OF ATUMATIC VALVES PER WELL | [7 empty] | 1 WELL/2 VALVE(SSV/SSSV)
SITE CONDITION |  |  | 6 | AS PER PROJECT REQUIREMENT | [7 empty] | REFER TO NOTE 1 IN PAGE 4(GENERAL NOTES)
PROCESS DATA |  |  | 7 | WELL DESIGN PRESSURE(PSI) | [7 empty] | 5000
|  |  | 8 | WELL OPERATING PRESSURE(PSI) | [7 empty] | 650
|  |  | 9 | WELL DESIGN TEMPERATURE(ᵒC) | [7 empty] | 105
|  |  | 10 | WELL OPERATING TEMPERATURE(ᵒC) | [7 empty] | 80
SSV/SSSV SPECIFICATION DATA |  |  | 11 | SSV SWEPT VOLUME/ CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 5 LITER/3000 PSI(NOTE 5)
|  |  | 12 | SSSV SWEPT VOLUME / CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 2.5 LITER/5000 PSI(NOTE 5)
|  |  | 13 | SSV OPEN& CLOSE TIME /SSSV OPEN&CLOSE TIME | [7 empty] | 2/8 (NOTE 5)
|  |  | 14 | SSV / SSSV CONNECTION SIZE | [7 empty] | 1/2" / 1/4"(NOTE 5)
WHCP ENCLOSURE |  |  | 15 | IP RATING | [7 empty] | IP 65(NOTE 1)
|  |  | 16 | NACE MR0175/ISO 15156 COMPLIANCE | [7 empty] | NOT REQUIRED EXCEPT FOR PSHH/ PSLL AS PER BELOW TABLE
|  |  | 17 | NAME PLATE | [7 empty] | BOTH TAG AND WELL NUMBER TO BE INCLUDED IN NAME PLATE
|  |  | 18 | MATERIAL OF WHCP AND ALL ACCESSORIES | [7 empty] | 316 SS (NOTE 1)
|  |  | 19 | PANEL ACCESSORIES | [7 empty] | AS MINIMUM AS PER PROJECT (NOTE 1,5)
HPU |  |  | 20 | NUMBER OF OIL TANK/ VOLUME FOR OIL TANK | [7 empty] | 2 TANKS /ONE AS THE MAIN OIL TANK AND ONE FOR SSSV RETURN LINE (NOTE 9)
|  |  | 21 | NUMBER OF ACCUMULATOR | [7 empty] | 2 NO. FOR HP/MP HEADERS (VTC)
|  |  | 22 | PUMP REQUIREMENT | [7 empty] | N2 DRIVEN AND HAND PUMPS(NOTE 1,3)
|  |  | 23 | PUMP MAX. WORKING PRESSURE | [7 empty] | 5000 PSI (EACH PUMPS SEPARATELY)
NITROGEN BOTTLES/ PNEUMATIC SUPPLY (PER PANEL) (NOTE 1,2) |  |  | 24 | NUMBER OF BOTTLES | [7 empty] | VENDOR TO ADVISE (CALCULATION TO BE PROVIDED)(NOTE 2)
|  |  | 25 | DIMENSIONS FOR BOTTLES RACK | [7 empty] | VENDOR TO ADVISE(NOTE 2)
|  |  | 26 | PRESSURE GAUGES FOR EACH HEADER | [7 empty] | REQUIRED(NOTE 1)
PANEL MOUNTED GAUGES |  |  | 27 | PRESSURE GAUGES ON PANEL FRONT | [7 empty] | FRONT FACE MOUNTED, AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
|  |  | 28 | PRESSURE GAUGES MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 29 | DIAL SIZE | [7 empty] | 60 mm
SSV/SSSV COMMAND TUBING(NOTE 8,9) |  |  | 30 | TUBE SIZE TO SSV/ SSSV(BY WHCP VENDOR) | [7 empty] | 1/2" / 1/4"(NOTE 5)
|  |  | 31 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 32 | TUBE LENGTH FROM WELL TO SSV/ SSSV (BY WHCP VENDOR) | [7 empty] | 30 m /30 m
FUSIBLE PLUG LOOP (NOTE 8,9) |  |  | 33 | TUBE SIZE | [7 empty] | 1/4"
|  |  | 34 | TUBE LENGTH TO AROUND WELL (BY WHCP VENDOR) | [7 empty] | 50m
|  |  | 35 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 36 | NUMBER OF FUSIBLE PLUG FOR EACH WELL/SET POINT | [7 empty] | 3 NO. (SET POINT:100ᵒC)
PANEL MOUNTED PUSH BUTTONS |  |  | 37 | ESD RESSET FUNCTION/SSV AND SSSV OPEN/CLOSE COMMAND FOR EACH WELL | [7 empty] | REQUIRED DEDICATED FRONT FACE PUSH BUTTONS AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
PANEL MOUNTED INDICATORS/ LAMPS |  |  | 38 | VALVES OPEN & CLOSE FEEDBACK STATUS | [7 empty] | REQUIRED DEDICATED FRONT FACE INDICATORS AS PER PROJECT DIAGRAMS(VTC)(NOTE 6,1)
PRESSURE PILOT |  |  | 39 | PRESSURE SWITCHES FOR PRESSURE SENSING LINE | [7 empty] | 4 NO. FOR EACH PANEL
SPARE PART |  |  | 40 | SPARE PARTS FOR COMMISSIONING AND START-UP | [7 empty] | REQUIRED(NOTE 1)
|  |  | 41 | SPARE PARTS FOR TWO YEARS OPERATION | [7 empty] | REQUIRED(NOTE 1)
INSPECTION & TEST |  |  | 42 | AS PER PROJECT REQUIREMENT | [7 empty] | REQUIRED(NOTE 1)
PURCHASE |  |  | 43 | MANUFACTURER | [7 empty] | FINALIZED BASED ON VENDOR DATA
|  |  | 44 | MODEL | [7 empty] | FINALIZED BASED ON VENDOR DATA
RELATED DATA SHEETS FOR PRESSURE SENSING LINE AND SWITCHES
TAG NO. | PSHH-1401A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 4200
TAG NO. | PSLL-1401A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 194.575
TAG NO. | PSHH-1401B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 202.71
TAG NO. | PSLL-1401B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W028-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1401 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 176.044
NOTE:
VTA : VENDOR TO ADVISE |  |  | VTC: VENDOR TO CONFIRM |  |  |  |  | NIA: NOT APPLICABLE
1- FOR DETAIL DATA REFER TO DOC.:SPECIFICATION FOR WHCP/HPU, BK-SSGRL-PEDCO-110-IN-SP-0001.
2- AS MINIMUM, BOTTLES WITH CAPACITY OF 50 LITER WITH QUANTITY: 4 MAIN BOTTLES AND 4 RESERVED BOTTLES SHALL BE CONSIDERED
3- NITROGEN GAS FOR N2 DRIVEN PUMP SUPPLY AT LEAST FOR TWO TIMES ACTUATION OF EACH VALVES (SSV AND SSSV) IS REQUIRED.
4- THE WHCP PANEL SHALL BE SUPPLIED WITH “FIRST OUT” FEATURE SO THE PANEL LOGIC SHALL BE DESIGNED IN A MANNER THAT FIRST CAUSE OF PANEL
SHUTDOWN BE DISTINGUISHABLE FOR MAINTENANCE PURPOSES.
5- TO BE FINALIZED BASED ON SSV/SSSV VENDOR FINAL DATA BOOK.
6- REFER TO "WHCP HYDRAULIC DIAGRAM,BK-SSGRL-PEDCO-110-IN-DG-0002".
7- ALL TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE SUPPLIED BY WHCP VENDOR
8- THE QUANTITY OF TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE FINALIZED BY WHCP VENDOR.
9- THE MINIMUM VOLUME OF OIL TANK(50 LITER) SHALL BE CONSIDERED IN ACCORDANCE TO THE CAPACITY OF SSV/SSSV AND THE HYDRAULIC OIL
LINE.
D03
D03
D03

## 035
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیت های رو زمینی در بسته های کاری تحت الارض عمومی و مشترک
DATA SHEETS FOR WHCP/HPU-WELLHEADS
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه
9184 – 073 - 053 |  |  |  | BK | SSGRL |  | PEDCO |  | 000 |  | IN | DT |  | 0001 | D03
WELLHEAD CONTROL PANEL FOR WELL NO. W035
GENERAL DATA |  |  | 1 | TAG NUMBERS | [7 empty] | WHCP-1501
|  |  | 2 | DIMENSIONS FOR PANEL | [7 empty] | VTA
|  |  | 3 | P&ID NO. | [7 empty] | BK-W035-PEDCO-110-PR-PI-0001
|  |  | 4 | HYDRAULIC DIAGRAM NO. | [7 empty] | BK-SSGRL-PEDCO-110-IN-DG-0002
|  |  | 5 | NUMBER OF WELLS PER WHCP /NUMBER OF ATUMATIC VALVES PER WELL | [7 empty] | 1 WELL/2 VALVE(SSV/SSSV)
SITE CONDITION |  |  | 6 | AS PER PROJECT REQUIREMENT | [7 empty] | REFER TO NOTE 1 IN PAGE 4(GENERAL NOTES)
PROCESS DATA |  |  | 7 | WELL DESIGN PRESSURE(PSI) | [7 empty] | 5000
|  |  | 8 | WELL OPERATING PRESSURE(PSI) | [7 empty] | 650
|  |  | 9 | WELL DESIGN TEMPERATURE(ᵒC) | [7 empty] | 105
|  |  | 10 | WELL OPERATING TEMPERATURE(ᵒC) | [7 empty] | 80
SSV/SSSV SPECIFICATION DATA |  |  | 11 | SSV SWEPT VOLUME/ CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 5 LITER/3000 PSI(NOTE 5)
|  |  | 12 | SSSV SWEPT VOLUME / CRACK OPEN HYDRAULIC PRESSURE | [7 empty] | 2.5 LITER/5000 PSI(NOTE 5)
|  |  | 13 | SSV OPEN& CLOSE TIME /SSSV OPEN&CLOSE TIME | [7 empty] | 2/8 (NOTE 5)
|  |  | 14 | SSV / SSSV CONNECTION SIZE | [7 empty] | 1/2" / 1/4"(NOTE 5)
WHCP ENCLOSURE |  |  | 15 | IP RATING | [7 empty] | IP 65(NOTE 1)
|  |  | 16 | NACE MR0175/ISO 15156 COMPLIANCE | [7 empty] | NOT REQUIRED EXCEPT FOR PSHH/ PSLL AS PER BELOW TABLE
|  |  | 17 | NAME PLATE | [7 empty] | BOTH TAG AND WELL NUMBER TO BE INCLUDED IN NAME PLATE
|  |  | 18 | MATERIAL OF WHCP AND ALL ACCESSORIES | [7 empty] | 316 SS (NOTE 1)
|  |  | 19 | PANEL ACCESSORIES | [7 empty] | AS MINIMUM AS PER PROJECT (NOTE 1,5)
HPU |  |  | 20 | NUMBER OF OIL TANK/ VOLUME FOR OIL TANK | [7 empty] | 2 TANKS /ONE AS THE MAIN OIL TANK AND ONE FOR SSSV RETURN LINE (NOTE 9)
|  |  | 21 | NUMBER OF ACCUMULATOR | [7 empty] | 2 NO. FOR HP/MP HEADERS (VTC)
|  |  | 22 | PUMP REQUIREMENT | [7 empty] | N2 DRIVEN AND HAND PUMPS(NOTE 1,3)
|  |  | 23 | PUMP MAX. WORKING PRESSURE | [7 empty] | 5000 PSI (EACH PUMPS SEPARATELY)
NITROGEN BOTTLES/ PNEUMATIC SUPPLY (PER PANEL) (NOTE 1,2) |  |  | 24 | NUMBER OF BOTTLES | [7 empty] | VENDOR TO ADVISE (CALCULATION TO BE PROVIDED)(NOTE 2)
|  |  | 25 | DIMENSIONS FOR BOTTLES RACK | [7 empty] | VENDOR TO ADVISE(NOTE 2)
|  |  | 26 | PRESSURE GAUGES FOR EACH HEADER | [7 empty] | REQUIRED(NOTE 1)
PANEL MOUNTED GAUGES |  |  | 27 | PRESSURE GAUGES ON PANEL FRONT | [7 empty] | FRONT FACE MOUNTED, AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
|  |  | 28 | PRESSURE GAUGES MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 29 | DIAL SIZE | [7 empty] | 60 mm
SSV/SSSV COMMAND TUBING(NOTE 8,9) |  |  | 30 | TUBE SIZE TO SSV/ SSSV(BY WHCP VENDOR) | [7 empty] | 1/2" / 1/4"(NOTE 5)
|  |  | 31 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 32 | TUBE LENGTH FROM WELL TO SSV/ SSSV (BY WHCP VENDOR) | [7 empty] | 30 m /30 m
FUSIBLE PLUG LOOP (NOTE 8,9) |  |  | 33 | TUBE SIZE | [7 empty] | 1/4"
|  |  | 34 | TUBE LENGTH TO AROUND WELL (BY WHCP VENDOR) | [7 empty] | 50m
|  |  | 35 | TUBE MATERIAL | [7 empty] | 316 SS (NOTE 1)
|  |  | 36 | NUMBER OF FUSIBLE PLUG FOR EACH WELL/SET POINT | [7 empty] | 3 NO. (SET POINT:100ᵒC)
PANEL MOUNTED PUSH BUTTONS |  |  | 37 | ESD RESSET FUNCTION/SSV AND SSSV OPEN/CLOSE COMMAND FOR EACH WELL | [7 empty] | REQUIRED DEDICATED FRONT FACE PUSH BUTTONS AS PER PROJECT DIAGRAMS (VTC)(NOTE 6,1)
PANEL MOUNTED INDICATORS/ LAMPS |  |  | 38 | VALVES OPEN & CLOSE FEEDBACK STATUS | [7 empty] | REQUIRED DEDICATED FRONT FACE INDICATORS AS PER PROJECT DIAGRAMS(VTC)(NOTE 6,1)
PRESSURE PILOT |  |  | 39 | PRESSURE SWITCHES FOR PRESSURE SENSING LINE | [7 empty] | 4 NO. FOR EACH PANEL
SPARE PART |  |  | 40 | SPARE PARTS FOR COMMISSIONING AND START-UP | [7 empty] | REQUIRED(NOTE 1)
|  |  | 41 | SPARE PARTS FOR TWO YEARS OPERATION | [7 empty] | REQUIRED(NOTE 1)
INSPECTION & TEST |  |  | 42 | AS PER PROJECT REQUIREMENT | [7 empty] | REQUIRED(NOTE 1)
PURCHASE |  |  | 43 | MANUFACTURER | [7 empty] | FINALIZED BASED ON VENDOR DATA
|  |  | 44 | MODEL | [7 empty] | FINALIZED BASED ON VENDOR DATA
RELATED DATA SHEETS FOR PRESSURE SENSING LINE AND SWITCHES
TAG NO. | PSHH-1501A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 4200
TAG NO. | PSLL-1501A | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 194.575
TAG NO. | PSHH-1501B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 202.71
TAG NO. | PSLL-1501B | P&IDs No. |  |  |  | OPER. TEMP. (°C) |  |  |  | SERVICE |  |  | PROCESS CON. OF SENSING LINE TO THE PIPE |  | FLUID | OPER. PRESS. (PSIG) | OVER RANGE PROT.
|  | BK-W035-PEDCO-110-PR-PI-0001 |  |  |  | 80 | [6 empty] | 1/2" |  | CRUDE OIL | 635.2 | REQUIRED
|  | LINE / EQUIPMENT NO. |  |  |  | DSG. TEMP. (°C) |  |  |  | PNEUMATIC LOGIC LINE(N2) OF WELLHEAD PANEL ACTUATED BY PROCESS FLUID FROM MAIN LINE |  |  | PRESS. ELEM.TYPE |  | PRESS. ELEM. MTR. | DESIGN PRESS. (PSIG) | SET POINT (PSIG)
|  | WHCP-1501 |  |  |  | 105 | [6 empty] | BY VENDOR |  | SS 316 | 5000 | 176.044
NOTE:
VTA : VENDOR TO ADVISE |  |  | VTC: VENDOR TO CONFIRM |  |  |  |  | NIA: NOT APPLICABLE
1- FOR DETAIL DATA REFER TO DOC.:SPECIFICATION FOR WHCP/HPU, BK-SSGRL-PEDCO-110-IN-SP-0001.
2- AS MINIMUM, BOTTLES WITH CAPACITY OF 50 LITER WITH QUANTITY: 4 MAIN BOTTLES AND 4 RESERVED BOTTLES SHALL BE CONSIDERED
3- NITROGEN GAS FOR N2 DRIVEN PUMP SUPPLY AT LEAST FOR TWO TIMES ACTUATION OF EACH VALVES (SSV AND SSSV) IS REQUIRED.
4- THE WHCP PANEL SHALL BE SUPPLIED WITH “FIRST OUT” FEATURE SO THE PANEL LOGIC SHALL BE DESIGNED IN A MANNER THAT FIRST CAUSE OF PANEL
SHUTDOWN BE DISTINGUISHABLE FOR MAINTENANCE PURPOSES.
5- TO BE FINALIZED BASED ON SSV/SSSV VENDOR FINAL DATA BOOK.
6- REFER TO "WHCP HYDRAULIC DIAGRAM,BK-SSGRL-PEDCO-110-IN-DG-0002".
7- ALL TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE SUPPLIED BY WHCP VENDOR
8- THE QUANTITY OF TUBE AND ACCESSORIES FOR SSV/SSSV, FUSIBLE PLUG AND INTERCONNECTION ON WHCP SHALL BE FINALIZED BY WHCP VENDOR.
9- THE MINIMUM VOLUME OF OIL TANK(50 LITER) SHALL BE CONSIDERED IN ACCORDANCE TO THE CAPACITY OF SSV/SSSV AND THE HYDRAULIC OIL
LINE.
D02
D03