## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-SSGRL-PEDCO-110-IN-DT-0001 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0374 |  |  | Transmittal Date: 21 Dec 2021
Document Title:Data Sheets For WHCP/HPU - Wellheads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0008-IN-TR-0374 |  |  | Transmital Date: 21 Dec 2021
[5 empty] | CRS No:PEDCO-CRS-BK-SSGRL-PEDCO-110-IN-DT-0001_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Format Data sheet for pressure switches are not acceptable. Standard format for switches shall be considered. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Modified. (This comment has been noted in last revision of document )
3 | Nace MR-0175 requirement shall be considered for WHCP. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Due to the client comment it has been added ( only for wetted part of high low switches, NACE is requested) (This comment has been noted in last revision of document)
4 | Tube and fittings specification shall be specified and scope of supply for mentioned items shall be illuminated clearly. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Modified.(Note 8 in the datasheet has been added for this item) (This comment has been noted in last revision of document)
5 | Hydraulic panel detail data like oil Tank, Level transmitters, pump data, accumulator, filters ... shall be specified. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | package detail shall be designed by vendor . Minimum requirements are specified in reference specification. ( All descriptions could not be repeated in data sheet) (This comment has been noted in last revision of document )
6 | Note that,Tube Length from Well to SSV \ SSSV will be finalized based on project document. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Noted.(Note 9 in the datasheet had added for this item) (This comment has been noted in last revision of document)
7 | Note that, Tube Length from Fusible Plug to Well will be finalized based on project document. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Noted.(Note 9 in the datasheet had added for this item) (This comment has been noted in last revision of document)
8 | Note -6 related to Fusible Plug Tube Size to be re-checked. Scope of supplies for Fusible Plugs shall be specified Clearly. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Noted.(Note 8 in the datasheet had added for this item) (This comment has been noted in last revision of document)
9 | Hold and Blank cells are not acceptable. Item 2 in previous CRS is not noted. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Noted. Modified. (This comment has been noted in last revision of document)
10 | Specify clearly the meaning of Number of Valves per Well. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Modified. It means number of Automate valves per well which shall be controlled by WHCP. (This comment has been noted in last revision of document)
11 | PANEL MOUNTED PUSH BUTTONS Section: - Regarding to WHCP hydraulic diagram,BK-SSGRL-PEDCO-110-IN-DG-0002_RevD01, ESD/Fusible Line Charge P.B to be specified. - Integrity between documents shall be considered. - Note that, This items will be finalized based on client requirements and vendor recommendation |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | All related documents are checked and modified for integrated data . (This comment has been noted in last revision of document)
12 | PANEL MOUNTED INDICATORS/ LAMPS Section: - Note that Indicators/Lamps shall be considered for SSV and SSSV. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Modified. All related documents are checked and modified for integrated data . (This comment has been noted in last revision of document)
13 | PANEL MOUNTED INDICATORS/GAUGES Section: - The Number and description for Pressure gauges and indicators shall be specified. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Minimum requirements are specified in diagram which shall be finalized by vendor. Note for reference diagram is added. (This comment has been noted in last revision of document )
14 | Page 5: Please note that: Manufacture and model will be finalized based on vendor data. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | It has been modified. (This comment has been noted in last revision of document )
15 | Process Comment: - All hold items (Process Data) should be specified in next revision. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Noted. (This comment has been noted in last revision of document)
16 | Process Comment: - Design temp. should be revised. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | Checked and Modified based on the latest process data. (This comment has been noted in last revision of document)
17 | Piping Comment: در جدول Data Sheet مربوطه در ستون Piping Class قبل از چوك كلاس خط LN15C و بعد از چوك كلاس خط LN15D مي باشد كه بايستي درج گردد. |  | BK-SUR-ENG-INS-00-02067 | 2021-11-20 | It had been modified. (This comment has been noted in last revision of document)
18 | با توجه به نهايي شدن برخي از آيتم ها بر اساس نظر وندور،مدرك پس از نهايي شدن پيشنهاد وندور مجدد بايستي بررسي گردد. |  | BK-SUR-ENG-INS-00-02519 | 2022-01-02 | این مدرک با توجه به آخرین تغییرات توافق شده طراحی و تهیه شده است و در حال حاضر ضمیمه قرارداد برای خرید WHCP می باشد، خواهشمند است تغییرات درخواستی رسما جهت اعمال در مدرک Vendor اعلام شود.
19 | با توجه به درخواست ذينفع اصلي پروژه در رابطه با قرار دادن يك PB بر روي فنس، اين مورد ذكر گردد. |  | BK-SUR-ENG-INS-00-02519 | 2022-01-02 | این مورد قبلا توسط کارفرمای محترم(NISOC ) اعلان شد و پاسخ آن تهیه و ارسال گردید که مطابق طراحی Basic و آخرین توافقات بروی این مدرک، PB بر روی فنس دیده نشده است.
20 | بر اساس نظر ذينفع اصلي پروژه جهت ضميمه كردن مدارك SSV,SSSV موضوع در يك نوت با مضمون زير يا مشابه آن اضافه گردد: The WHCP, tubing, connections, Pressure/Temperature ratings shall meet all requirement referred to Oil & Gas SSV-s and SSSV data sheets and Process Data: |  | BK-SUR-ENG-INS-00-02519 | 2022-01-02 | آخرین اطلاعاتSSSV/SSV مطابق نامه نگاری های انجام شده در اختیار سازنده WHCP قرار داده شده است، خواهشمند است تغییرات احتمالی رسما جهت اعمال در مدرک Vendor اعلام شود.
21 | نقطه نظرات بخش فرايند به شرح زير مي باشد: 1- بنظر مي رسد Set point براي PSLL-1101 A و سويچ هاي مشابه در مابقي پكيج هاي كنترل نياز به بازنگري دارد. 2- شرايط محيطي اعلام شده با آخرين اطلاعات مندرج در مدارك فرايندي مطابقت ندارد |  | BK-SUR-ENG-INS-00-02519 | 2022-01-02 | مدرک مطابق مدارک فرآیندی اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and inculpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 02 Jan 2022 |  |  |  |  | Date: