## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0006 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0668 |  |  | Transmital Date: 3/5/2022
Document Title: P&ID - 1st Stage Gas Compression Suction Drums |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-0668 |  |  | Transmital Date: 3/5/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0006_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نظرات عمومی |  | 1401-2294-23096 | 1401/01/26 | پاسخ کلیه‌ نظرات عمومی در پاسخنامه به شماره NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0002_D02 موجود است.
2 | ترنسمیتر فشار در نظر گرفته شده در اسناد پیمان یک تجهیز ایمنی و ارتباط با کنترل فشار در نظر گرفته شده ندارد |  | 1401-2294-23096 | 1401/01/26 | با توجه به چیدمان جدید ُ تجهیز مذکور در ورودی کمپرسور در نظر گرفته شده است.
3 | کاهنده های اطراف شیرهای PCV-2123A/B/C به صورت 6”*H” نوشه شده است که باید تصحیح گردد. |  | 1401-2294-23096 | 1401/01/26 | اصلاح شد.
4 | استفاده از شیر برقی XV (ON/OFF) برای کنترل مایعات مخازن V-2101A/B/C با توجه به فاصله کم بین سطح (LLL) و سطح زیاد مایع (HLL) در مخزن ذکر شده (30 سانتی متر) ممکن است مرتب باعث باز و بسته شدن شیر برقی یاد شده گردد. لذا پیشنهاد می گردد در این خصوص بررسی های لازم به عمل آمده و در صورت صلاحدید از شیرهای LCV استفاده گردد. |  | 1401-2294-23096 | 1401/01/26 | با توجه به میزان کم مایع و همچنین توضیحات ارائه شده در جلسه مهندس pid REVIEW مقرر گردید شیر از نوع ON/OFF باشد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: