## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0008 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0668 |  |  | Transmital Date: 05.Mar.2022
Document Title: P&ID - 1st Stage Gas Compression Air Coolers |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-0668 |  |  | Transmital Date: 05.Mar.2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-PR-PI-0008_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | بصورت عمومي در تمام PID ها در جلسه 27-11-1400 مقرر گرديد كه نمايش نوع اتصال شيرها (فلنجي/ جوشي و...) نمايش داده شود كه اين مهم در اين ويرايش انجام نپذيرفته است. |  | BK-SUR-ENG-PCS-01-03755 | 09.Apr.2022 | اعمال گردید.
2 | كلاس CS00 براي خط خروجي از كولر استفاده شده كه دماي طراحي آن با توجه به Criteria با مدرك PMS مطابقت ندارد. |  | BK-SUR-ENG-PCS-01-03755 | 09.Apr.2022 | مطابق نتایج مطالعات خوردگی در نظر گرفته شده و در صورت نیاز مدرک pms بازنگری میگردد.
3 | محل تغيير كلاس مشخص گردد. |  | BK-SUR-ENG-PCS-01-03755 | 09.Apr.2022 | اعمال گردید.
4 | پايپينگ: درصد شيب مشخص گردد. |  | BK-SUR-ENG-PCS-01-03755 | 09.Apr.2022 | اعمال گردید.
5 | ابزاردقيق: اختصار HY در مدرك S&L مشخص شود، همچنين در خصوص عملكرد آنها شفاف سازي صورت پذيرد. |  | BK-SUR-ENG-PCS-01-03755 | 09.Apr.2022 | اعمال گردید.
6 | لازم است نقطه نظرات ذينفع اصلي اعمال گردد. |  | BK-SUR-ENG-PCS-01-03755 | 09.Apr.2022 | اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: 24/08/2021