## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-PR-PI-0022 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0670 |  |  | Transmital Date: 3/5/2022
Document Title: P&ID - Fuel Gas System |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-PR-TR-0670 |  |  | Transmital Date: 3/5/2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0022_D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نظرات عمومی |  | 1401-2294-33690 | 1401/02/01 | پاسخ کلیه‌ نظرات عمومی در پاسخنامه به شماره NISOC-CRS-BK-GCS-PEDCO-120-PR-PI-0020_D02 موجود است.
2 | علت تغییر در فلسفه کنترل مخزن گاز که در اسناد پیمان در نظر گرفته شده است توضیح داده شود. |  | 1401-2294-33690 | 1401/02/01 | در مدارک پیمان از دو عدد شیر کنترلی استفاده شده بود که با توجه به وجود مسیر کنار گذر و حجم کم گاز نیازی به در نظر گرفتن دو شیر کنترلی به صورت موازی
3 | - برای میزان کم مایع در مخزن قطره گیر گاز ، سطح ESD یک در نظر گرفته شده است که اشتباه است. (اشاره به نوت 2) |  | 1401-2294-33690 | 1401/02/01 | اصلاح گردید.
4 | - سناریو تخلیه مایعات مخزن مطابق اسناد پیمان در نظر گرفته شود. |  | 1401-2294-33690 | 1401/02/01 | با توجه به حجم کم مایعات و توضیحات ارائه شده در جلسات مهندسی PID Review ، استفاده از شیر کنترلی مناسب نبوده و بر این اساس از شیر ON/OFF استفاده میگردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: M.Fakharian | Signature
| Date: |  |  |  |  | Date: