## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-ME-DT-0005_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0401 |  |  | Transmital Date: 08/DeC/2021
Document Title:Mechanical Data Sheets For 2nd Stage Gas Air Coolers |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0103-ME-TR-0401 |  |  | Transmital Date: 08/DeC/2021
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-BK-GCS-PEDCO-120-ME-DT-0005_D00 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | آخرين نسخه ديتا شيت برقي موتورهاي فشار ضعيف (ارسالي با ترنسميتال 1223) كه مورد تاييد اين مديريت و ذينفع اصلي قرار گرفته است در پيوست مدرك اضافه گردد. در ضمن عنوان و شماره مدرك مذكور در نوت 9 اصلاح گردد |  | BK-SUR-ENG-MEC-00-02838 | 2022-01-29 | ترنسمیتال 1223 هنوز از طرف مشاور ارسال نشده است. همچنین آخرین ویرایش استاندارد موتورهای LV شماره IPS-M-EL-131(2) می باشد. لازم به ذکر است مدرک دیتاشیت برای موتورهای LV مدرک شماره “BK-GCS-PEDCO-120-EL-DT-0008” می باشد. لذا ابهامی در نوت شماره 9 از مدرک مکانیک وجود ندارد.
2 | Summer case duty is more than Winter Case |  | BK-SUR-ENG-MEC-00-02838 | 2022-01-29 | Note is revised.
3 | Auto Fan pitch control also needed. |  | BK-SUR-ENG-MEC-00-02838 | 2022-01-29 | It was already considered at Fan section, (Pitch adjusment) and it was also refered to Note 4, 7.
4 | According to P&ID(BK-GCS-PEDCO-120-PR-PI-0008_D01), Half of fans shall be equipped with variable pitch automatic system to control fluid outlet temperature" , So TCVs shall be considered for this purpose. |  | BK-SUR-ENG-MEC-00-02838 | 2022-01-29 | It was already considered at Fan section, (Pitch adjusment) and it was also refered to Note 4, 7.
5 | These data are not in the PR DS - Nozzle (Vent, Drain) - Tube (O.D , thickness) - Fin (Type, material) |  | BK-SUR-ENG-MEC-00-02838 | 2022-01-29 | - Vent & Drain are based on P&ID -Revised -Revised
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: P.BAVARSAD | Signature | H.naserizadeh |  |  | Clarified By: H.Adineh | Signature
| Date: 1/29/2022 |  |  |  |  | Date: 6/18/2022