## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR FIRE WATER STORAGE TANK
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | ME | DT | 0017 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
MECHANICAL DATA SHEETS FOR FIRE WATER STORAGE TANK
نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | JUN.2022 |  | IFC |  |  |  | H.Adineh |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: |  |  | F0Z-708848
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR FIRE WATER STORAGE TANK
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | ME | DT | 0017 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | [7 empty] | 70
7 | X | [7 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Note 1
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR FIRE WATER STORAGE TANK
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 7
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | ME | DT | 0017 | D00
General Notes
| 1. | The asterisk * denotes information and/or confirmation required from vendor. the vendor shall be fully responsible for design
and supply of the tank. the tank shall be supplied in accordance with project "Specification For Atmospheric Above Ground Welded
Steel Tanks.
| 2. | The VENDOR/BIDDER shall design and supply the storage tank in accordance with "Specification For Atmospheric Above Ground
Welded Steel Tanks" , Document No.: "BK-GNRAL-PEDCO-000-ME-SP-0002" and "Standard Detail Drawing For Storage Tanks",
| 3. | Document No.: BK-GNRAL-PEDCO-000-ME-DW-0002'. VENDOR/BIDDER shall provide completed datasheets with bid.
| 4. | Tank height shall be checked based on Freeboard calculation by vendor.
| 5. | The VENDOR/BIDDER shall be fully responsible for the complete mechanical design of the tank.
| 6. | External and internal surface of tank shall be coated in accordance with BK-GNRAL-PEDCO-000-PI-SP-0006 &
BK-GNRAL-PEDCO-000-PI-SP-0007 respectively.
| 7. | All materials for pressure parts shall fulfill the impact test requirements of API-650 standard.
| 8. | For standard detail of earth lug execution refer to the project "standard detail drawing for storage tanks
Doc. NO. "BK-GNERL-PEDCO-000-ME-DW-0002" and provide minimum two earthing terminals and two cables per tank.
| 9. | Manways shall be supplied complete with blind flange, external grab handles, internal grab handle and ladder rungs, nuts,
bolting, gasket and proof load test davits. Davits shall be proof load tested on the vessel to 1.5 x Safe Working Load (SWL)
and shall be marked accordingly.
| 10. | Instrument and piping nozzle flanges shall be in accordance with ASME B 16.5.
| 11. | Minimum width of shell courses plates shall be 1.5 m.
| 12. | Stairways shall meet the requirements of for IPS-G-ME-100 (Sec. 3.8.10), IPS-D-CE-141 & IPS-D-CE-142 and IPS-E-SF-400.
The angle of stairways to horizontal plane shall not exceed 45°.
| 13. | If any imposed load (by nozzles or their connections) causes high local stress in any part of shell and roof, the subjected
component shall be investigated according to appendix ‘P’ of API Std. 650.
| 14. | Cone roof angle and roof plates joint shall be so selected that tank roof plate thickness will not be greater than 12mm.
| 15. | All nozzles equal / greater than 2" shall have reinforcement pad.
| 16. | All nozzles connection weld to tank shall be with full penetration.
| 17. | Necessity of wind girder and stiffening ring will be finalized by vendor.
| 18. | Allowable stress of anchor bolts shall not be greater than those are recommended in API 650 standard.
| 19. | The requirement of internal and external cathodic protection shall be considered by VENDOR.
| 20. | Seal materials shall have enough resistance against temperature changes, expansion & contraction, fluid weight changes and etc.
| 21. | All dimensions are in "mm" unless otherwise specified.
| 22. | Vent size and quantity shall be specified/verified by vendor according to API 2000.
| 23. | Projection of Horizontal and Vertical nozzles are specified from tank centerline and top of top angle (roof line) respectively.
| 24. | For standard detail of earth lug execution refer to the project "standard detail drawing for storage tanks DOC. NO.
"BK-GNRAL-PEDCO-000-ME-DW-0002" and provide minimum two earthing lugs and two cables per tank.
| 25. | All nozzle loads shall not be less than specified values in the"Specification For Atmospheric Above Ground Welded Steel Tanks" ,
Welded Steel Tanks" , Document No.: "BK-GNRAL-PEDCO-000-ME-SP-0002"
| 26. | Will be Finalized later.

## Gen. Inf.
NISOC | [6 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR FIRE WATER STORAGE TANK
شماره پیمان: | [6 empty] | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال |  |  | نسخه |  | شماره صفحه: 4 از 7
9184 – 073 - 053 | [6 empty] | BK | GCS |  | PEDCO |  | 120 |  | ME |  | DT | 0017 |  |  | D00
Rev. | GENERAL INFORMATION (TO BE COMPLETED BY PURCHASER)
| 1 | 1. PURCHASER / AGENT: |  |  |  | NISOC
| 2 |  | ADDRESS:
| 3 |  | CITY: |  | Bushehr |  |  | PROV.: | [7 empty] | POSTAL CODE: | [6 empty] | PHONE:
| 4 | 2. USER:
| 5 | 3. ERECTION SITE: |  |  |  |  | NAME OF PLANT: |  |  | Binak
| 6 | [5 empty] | LOCATION: |  | BINAK, 20 km NORTHWEST of GENAVEH CITY
| 7 | 4. TANK NO.: |  | TK-2301 A / B |  |  | NOMINAL CAPACITY: |  |  |  | 1260 | [5 empty] | m3 |  | NET WORKING CAPACITY: | [5 empty] | 1040 |  |  |  | m3
| 8 |  | QTY. REQ'D: |  | 2 Sets |  | OVERFILL PROTECTION (API RP 2350): | [9 empty] | m
| 9 | 5. PUMPING RATES: |  |  |  |  | IN |  |  |  |  | (Note(26) |  |  |  | m3/hr | OUT | [6 empty] | (Note(26) |  | m3/hr
| 10 | 6. MIN./MAX. OPERATING TEMPERATURE: | [7 empty] | AMB. | [5 empty] | oC
| 11 | 7. PRODUCT STORED: | [6 empty] | Fire Water Tank | [9 empty] | DESIGN SPEC. GRAVITY: |  |  |  |  | 1 |  | AT | 163 |  | oC
| 12 | DESIGN TEMPERATURE: | [7 empty] | 85 | [5 empty] | oC |  |  | VAPOR PRESSURE: | [9 empty] | kPa
| 13 | 8. CORROSION ALLOWANCE:
| 14 | [5 empty] | SHELL: |  |  |  | 1.6 |  |  |  |  | mm |  |  | ROOF: |  |  |  |  | 1.6 |  |  |  |  | mm
| 15 | [5 empty] | BOTTOM: |  |  |  | 1.6 |  |  |  |  | mm |  |  | STRUCTURALS: |  |  |  |  | - |  |  |  |  | mm
| 16 | 9. SHELL DESIGN: |  |  |  |  | BASIC STANDARD API 650 |  |  | YES |  |  |  |  | APPENDIX A |  | YES |  | APPENDIX F |  | YES |  | IPS-G-ME-100 |  | YES |  | IPS-G-ME-110
| 17 | [5 empty] | DESIGN PRESSURE : |  |  |  | ATM+Full water | [5 empty] | kPa (g)
| 18 | 10. ROOF DESIGN: |  |  |  |  | BASIC STANDARD API 650 |  |  | YES |  |  |  |  | IPS-G-ME-100 |  | YES |  | IPS-G-ME-110 |  |  | NO
| 19 | [5 empty] | APPENDIX G (ALUMINUM DOME) | [5 empty] | NO |  |  |  | `
| 20 | [5 empty] | FRANGIBLE ROOF JOINT | [5 empty] | NO
| 21 | 11. ROOF DESIGN INFORMATION:
| 22 |  | UNIFORM LIVE LOAD: | [7 empty] | 1.2 |  |  |  |  | kPa (g)
| 23 |  | SPECIAL LOADS (PROVIDE SKETCH): | [12 empty] | kPa (g)
| 24 |  | INSULATION LOAD: | [7 empty] | - |  |  |  |  | kPa (g)
| 25 |  | MAXIMUM DESIGN ROOF TEMPERATURE: | [12 empty] | oC
| 26 |  | GASES IN THE VAPOUR SPACE:
27
| 28 | 12. EARTHQUAKE DESIGN : | [13 empty] | (APPENDIX E) |  |  | ROOF TIE RODS (5.10.4.5) :
| 29 | [5 empty] | SEISMIC ZONE: |  |  |  | (ASCE7-10) | [7 empty] | IMPORTANCE FACTOR |  |  |  |  | 1.25 | Fa : 1 |  |  | Fv : 1.5
| 30 | [5 empty] | SITE CLASS: |  |  |  | D | [7 empty] | SITE COEFFICIENT: |  |  |  |  | 1.2 | Ss : 1.25 |  |  | S1 : 0.58
| 31 | 13. WIND LOAD:
| 32 | [5 empty] | VELOCITY: |  |  |  | 120 |  |  |  |  | km/hr |  |  | ( DIRECTION: NW TO SE)
| 33 | [5 empty] | PROVIDE INTERMEDIATE WIND GIRDER (5.9.7) :
| 34 | 14. ENVIRONMENTAL EFFECTS:
| 35 | [5 empty] | MAXIMUM RAINFALL | [8 empty] | mm/year |  |  | TOTAL SNOW ACCUMULATION | [9 empty] | mm
36
| 37 | 15. SIZE RESTRICTIONS:
| 38 | [5 empty] | MAXIMUM DIAMETER | [5 empty] | 13000 |  |  | mm |  |  | MAXIMUM HEIGHT | [6 empty] | 9500 |  |  | mm
| 39 | 16. FOUNDATION TYPE: | [11 empty] | CONCRETE RINGWALL |  |  |  | YES
| 40 | [5 empty] | EARTH | [14 empty] | OTHER
| 41 | 17. APPLICABLE STANDARDS:
| 42 | [5 empty] | API 650 |  |  |  |  | & |  |  |  | IPS-G-ME-100 (1)
| 43 | 17. SERVICE TYPE
| 44 | [5 empty] | SOUR | NO |  |  |  | NON-SOUR |  |  |  | NO
| 45 | [5 empty] | LETHAL |  |  |  |  | NON-LETHAL
| 46 | 18. NACE REQUIREMENT
| 47 | [5 empty] | SSC | NO |  |  |  | HIC |  | NO
| 48 | REMARKS:
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66

## Const.
NISOC | [8 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR FIRE WATER STORAGE TANK
شماره پیمان: | [8 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  |  | شماره صفحه: 5 از 7
9184 – 073 - 053 | [8 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | ME |  | DT |  | 0017 |  | D00
Rev. | CONSTRUCTION DETAILS (TO BE COMPLETED BY MANUFACTURER AND/OR PURCHASER)
| 1 | 1. MANUFACTURER
| 2 |  | ADDRESS:
| 3 |  | CITY: | [9 empty] | PROV.: | [7 empty] | POSTAL CODE: | [6 empty] | PHONE:
| 4 | SERIAL NUMBER:
| 5 | 2. FABRICATOR:
| 6 |  | ADDRESS:
| 7 |  | CITY: | [9 empty] | PROV.: | [7 empty] | POSTAL CODE: | [6 empty] | PHONE:
| 8 | SERIAL NUMBER:
| 9 | 3. MATERIAL SPECIFICATIONS:
| 10 | SHELL : | [8 empty] | A-283 GR.C | [10 empty] | PIPE : |  |  |  | A-106 GR.B
| 11 | ROOF : | [8 empty] | A-283 GR.C | [10 empty] | FLANGE : |  |  |  | A-105
| 12 | BOTTOM / ANNULAR BOTTOM : | [8 empty] | A-283 GR.C | [10 empty] | EXT. BOLT / NUT : |  |  |  | A-193 GR.B7 / A-194 GR.2H
| 13 | FIXED INTERNALS : | [8 empty] | C.S. | [10 empty] | INT. BOLT / NUT : |  |  |  | S.S.
| 14 | REMOVABLE INTERNALS : | [8 empty] | -
| 15 | STRUCTURALS : | [8 empty] | A-36
| 16 | 4. NO. OF SHELL COURSES
| 17 | 5. PLATE WIDTHS AND THICKNESSES (INCLUDING CORROSION ALLOWANCE) | [16 empty] | (NOTE 11)
| 18 |  |  | 1. | 1500 | [6 empty] | 4. | 1500 | [6 empty] | 7. | 1500 | [5 empty] | 10.
| 19 |  |  | 2. | 1500 | [6 empty] | 5. | 1500 | [6 empty] | 8. | [6 empty] | 11.
| 20 |  |  | 3. | 1500 | [6 empty] | 6. | 500 | [6 empty] | 9. | [6 empty] | 12.
21
| 22 | 6. TANK BOTTOM: | [5 empty] | PLATE THICKNESS | [9 empty] | mm | (Note 1) |  |  | YES | LAP |  |  |  | BUTT |  | SEAMS
| 23 | [6 empty] | SLOPE | [6 empty] | 1 :120 |  |  | mm per meter |  |  |  |  | TO |  | YES |  | FROM |  | CENTER
| 24 | 7. MINIMUM WIDTH AND THICKNESS OF BOTTOM ANNULAR PLATES (5.5) : | [16 empty] | - |  |  |  | mm | (Note 1)
| 25 | 8. ROOF-TO SHELL DETAIL (FIGURE F-2 'API-650') : | [11 empty] | Detail B | [5 empty] | (Note 14)
| 26 | 9. INTERMEDIATE WIND GIRDER : | [7 empty] | (Note 18) | [5 empty] | NO |  |  | TOP WIND GIRDER FOR USE AS WALKWAY :
27
| 28 | 10. ROOF TYPE : |  |  |  | YES |  | CONE (Supported) | [5 empty] | DOME | [5 empty] | SPHERE
| 29 | [5 empty] | SLOPE OR RADIUS : | [6 empty] | 1 : 5 |  |  | (Note 14) | [9 empty] | `
| 30 | 11. ROOF PLATE: THICKNESS | [7 empty] | (Note 1) |  |  |  |  | mm | YES |  | LAP |  |  | BUTT |  | JOINT
| 31 | 12. PAINT: | [7 empty] | (Note 6)
| 32 |  |  | SHELL : | [5 empty] | EXTERIOR |  |  |  | YES | [7 empty] | INTERIOR |  |  |  | YES
| 33 |  |  |  |  | SURFACE PREPARATION
| 34 |  |  | BOTTOM : | [5 empty] | UNDERSIDE |  |  |  | YES | [7 empty] | INTERIOR |  |  |  | YES
| 35 |  |  |  |  | SURFACE PREPARATION
| 36 |  |  | ROOF : | [5 empty] | EXTERIOR | [11 empty] | INTERIOR |  |  |  | YES
| 37 |  |  |  |  | SURFACE PREPARATION
| 38 |  |  | STRUCTURAL STEEL : | [5 empty] | EXTERIOR |  |  |  | YES | [7 empty] | INTERIOR |  |  |  | -
| 39 |  |  |  |  | SPECIFICATION :
| 40 | 13. TANK BOTTOM COATING: | [7 empty] | INTERIOR |  |  |  | YES | [7 empty] | MATERIAL
| 41 |  |  |  |  | APPLICATION SPECIFICATION
| 42 | 14. INSPECTION BY: | [7 empty] | SHOP |  |  |  |  | FILED
| 43 | 15. WELD EXAMINATION: | [8 empty] | Radiograph (extent of radiography as per IPS-G-ME-100)
| 44 | [10 empty] | Supplementary liquid penetrant or ultrasonic
| 45 |  | JOINT EFFICIENCY: | [8 empty] | As Per Code
| 46 | 16. FILMS : | [19 empty] | PROPERTY OF
| 47 | 17. LEAK TESTING:
| 48 | [8 empty] | BOTTOM |  | YES |  |  | ROOF |  | YES |  | SHELL |  | YES
| 49 | 18. MILL TEST REPORTS: | [7 empty] | REQUIRED
| 50 | [8 empty] | PLATE | [8 empty] | STRUCTURAL SHAPES
| 51 | 19. PURCHASER'S REFERENCE DRAWING :
| 52 | 20. TANK SIZE : | [7 empty] | DIAMETER |  |  | 13000 |  |  |  |  | mm | HEIGHT |  | 9500 |  |  |  | mm
| 53 | DATE OF STANDARD 650 EDITION/REVISION : | [10 empty] | 12th Edition Aug 2018
54
55
56
57
58
59
60
61
62
63
64
65
66

## Appurt.
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR FIRE WATER STORAGE TANK
شماره پیمان: |  |  |  |  | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک | سریال |  |  | نسخه |  |  | شماره صفحه: 6 از 7
9184 – 073 - 053 |  |  |  |  | BK |  | GCS |  | PEDCO | 120 |  | ME |  | DT | 0017 |  |  | D00
Rev. | APPURTENANCES (TO BE COMPLETED BY MANUFACTURER AND/OR PURCHASER)
| 1 | 1. STAIRWAY STYLE |  | (Note 12) |  | YES |  | CIRCULAR | [5 empty] | STRAIGHT |  |  |  | ANGLE TO HORIZONTAL | [6 empty] | DEGREES
| 2 | [6 empty] | ROLLING LADDER
| 3 | 2. WALKWAY: | [5 empty] | WIDTH | [5 empty] | mm |  |  |  | LENGTH | [7 empty] | mm
| 4 | 3. DRAW -OFF SUMP: |  |  |  | YES |  | STANDARD | [5 empty] | SPECIAL
| 5 | 4. BOLTED DOOR SHEET : |  |  |  | NO | [6 empty] | (APPENDIX A TANKS ONLY) | [6 empty] | RAISED |  |  |  | FLUSH
| 6 | 5. SCAFFOLD HITCH
| 7 | 6. INTERNAL PIPING: | [5 empty] | SWING LINE | [5 empty] | SUCTION LINE
| 8 | [6 empty] | HEATING COIL SURFACE AREA | [9 empty] | m2
| 9 | 7. ROOF DRAIN: | [5 empty] | HOSE | [5 empty] | JOINTED
| 10 | [6 empty] | SIPHON
| 11 | 8. NO. AND SIZE OF SHELL MANHOLES |  |  |  |  | 2 x 24"
| 12 | 9. NO. AND SIZE OF ROOF MANHOLES |  |  |  |  | 1 x 24"
| 13 | SHELL NOZZLES LIST (Notes 1,15,16, 22)
| 14 | MARK | QTY. | DESCRIPTION |  |  |  |  | PIPE |  |  |  |  | FLANGE |  |  |  |  | PROJ. |  |  | REINF. |  |  | REMARKS
| 15 | [7 empty] | Size(in.) | Thk. |  | Sch. |  | Type | Rate. |  | Face |  | (mm) |  |  | Thk. |  | O.D.
| 16 | A | 1 | Inlet |  |  |  |  | 3 |  |  |  |  | WN | 150 # |  | RF |  | 6650
| 17 | B1 | 1 | Outlet |  |  |  |  | 12 |  |  |  |  | WN | 150 # |  | RF |  | 6750
| 18 | TL | 1 | Test Line |  |  |  |  | 10 |  |  |  |  | WN | 150 # |  | RF |  | 6750
| 19 | PSV | 1 | Pressure Safty Valve |  |  |  |  | 10 |  |  |  |  | WN | 150 # |  | RF |  | 6750
| 20 | LS | 2 | Level Switch |  |  |  |  | 2 |  |  |  |  | WN | 300 # |  | RF |  | 6650
| 21 | B2 | 1 | Over Flow |  |  |  |  | 3 |  |  |  |  | WN | 150 # |  | RF |  | 6650
| 22 | D | 1 | Drain |  |  |  |  | 3 |  |  |  |  | WN | 150 # |  | RF |  | 6650
| 23 | M1 | 2 | Manhole |  |  |  |  | 24 |  |  |  |  | WN | 150 # |  | RF |  | 6800
| 24 | LT | 2 | Level Transmitter |  |  |  |  | 2 |  |  |  |  | WN | 300 # |  | RF |  | 6650
25
26
| 27 | ROOF NOZZLES LIST (Notes 1, 23)
| 28 | MARK | QTY. | DESCRIPTION |  |  |  |  | PIPE |  |  |  |  | FLANGE |  |  |  |  | PROJ. |  |  | REINF. |  |  | REMARKS
| 29 | [7 empty] | Size(in.) | Thk. |  | Sch. |  | Type | Rate. |  | Face |  | (mm) |  |  | Thk. |  | O.D.
| 30 | V | 1 | Vent |  |  |  |  | 8 |  |  |  |  | WN | 150 # |  | RF |  | SEE DWG
| 31 | L1 | 1 | Level Indicator |  |  |  |  | 2 |  |  |  |  | WN | 300 # |  | RF |  | SEE DWG
| 32 | M2 | 1 | Roof Manhole |  |  |  |  | 24 |  |  |  |  | WN | 150 # |  | RF |  | SEE DWG
33
34
| 35 | TOTAL WEIGHT (kg) (Note 26)
| 36 | FABRICATION |  |  | OPERATION | [5 empty] | HYDROSTATIC TEST |  |  |  |  | REMOVABLE STANDARD | [6 empty] | LADDER & PLATFORM
37
38
| 39 | LOADING (Note 26)
| 40 | WINDSHEAR (KG) |  |  |  |  | WIND OVERTURNING MOMENT (KG.M) | [6 empty] | EARTHQUAKE SHEAR (KG) | [6 empty] | EARTHQUAKE OVERTURNING MOMENT (KG.M)
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66

## Gen. View
NISOC | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
MECHANICAL DATA SHEETS FOR FIRE WATER STORAGE TANK
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 7
9184 – 073 - 053 | BK | GCS | PEDCO | 120 | ME | DT | 0017 | D00
GENERAL ARRANGEMENT VIEW