## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-ME-DT-0002_D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0851 |  |  | Transmital Date: 20/Apr/2022
Document Title: DATA SHEETS FOR POTABLE WATER TANK OF WELL PADS |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-ME-TR-0851 |  |  | Transmital Date: 20/Apr/2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-ME-DT-0002_D01 |  |  | CRS Status:
| Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | با توجه به تغییر حجم مخزن نسبت به ویرایش قبل، ضروری است محاسبات مربوطه ارایه گردد. |  | 01/2294/54998 | 1401/02/19 | ه استحضار می رساند مدرک محاسبات WATER TANK OF WELL PADS در مدارک پروژه موجود نمی باشد. محاسبات صورت گرفته توسط این پیمانکار به شرح پیوست در نظر گرفته شده است.
2 | با توجه به موارد مندرج در بخش 10،2،2،3 کتابچه اسناد پیمان (برق رسانی به تلمبه های درون چاهی ) می بایست طراحی و محاسبه مخزن آب به همراه سازه مربوطه انجام پذیرد. |  | 01/2294/54998 | 1401/02/19 | نظرات کارفرمای محترم اعمال گردید.
3 | با توجه به مرتفع بودن مخزن، چه تمهیداتی جهت آبگیری مخزن در نظر گرفته شده است. |  | 01/2294/54998 | 1401/02/19 | پمپ پرکن پرتابل همواره با تانکر مربوطه می باشد.
4 | با توجه به شرایط محیطی، برای مخزن عایقکاری در نظر گرفته شود. |  | 01/2294/54998 | 1401/02/19 | برای این مخزن سایه بان در نظر گرفته شده است.
5 | با در نظر گرفتن دمای طراحی، شرایط محیطی، نحوه نصب و موارد مشابه در دیگر پروژه ها پیشنهاد می شود جنس مخزن فلزی در نظر گرفته شود. |  | 01/2294/54998 | 1401/02/19 | جنس مخزن از پلی اتیلن سه لایه (Food Grade) و محافظ در برابر اشعه UV آفتاب درنظر گرفته شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature | H.naserizadeh |  |  | Clarified By: H.Ghadyani | Signature | M.Fakharian
Date: