## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL /ESD SYSTEM
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | IN | LI | 0002 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST FOR CONTROL/ESD SYSTEM نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | JUN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-708609
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL /ESD SYSTEM
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | IN | LI | 0002 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | [7 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## NOTE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL /ESD SYSTEM
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | IN | LI | 0002 | D00
REFERENCES:
| P&ID - GAS PIPELINE (TO SIAHMAKAN G.I. STATION) | [7 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D02
| P&ID - CONDENSATE PIPELINE (TO BINAK PU) | [7 empty] | BK-PPL-PEDCO-320-PR-PI-0002_D02
| P&ID - SYMBOL & LEGEND for PFD and P&ID | [7 empty] | BK-PPL-PEDCO-320-PR-PI-0003_D01
NOTES:
| NOTE 1 : | ALL OF ANALOUGE TRANSMITTERS (AI/AO) SHALL BE CONSIDERED INTRINSICALLY SAFE (EEXIA) & ALL OF DIGITAL TRANSMITTERS (DI/DO) ARE NON INTRINSICALLY SAFE (EEXD).
| NOTE 2 : | I/O CARDS & ACCESSORIES SHALL BE SELECTED IN ACCORDANCE WITH '' SPECIFICATION FOR CONTROL SYSTEM".
| NOTE 3 : | ESD EQUIPMENT & ALL OF EQUIPMENT THAT IS ASSIGNED IN A CONTROL LOOP, ARE REDUNDANT.

## SUMMARY
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL /ESD SYSTEM
شماره پیمان: | [5 empty] | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 6
9184 – 073 - 053 | [5 empty] | BK | PPL |  | PEDCO | 320 | IN | LI | 0002 | D00
IO SIGNALS SUMMERY COUNT(TO/FROM GCS-DCS) SHALL BE CONSIDERED IN GCS-DCS SYSTEM I/O COUNT( INCLUDED IN OTHER WORK PACK)
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 |  | DI-NIS-NR |  | NIS | NR |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, NON-REDUNDANT) | [6 empty] | 2 |  | 3 | NOTES 1,2,3
| 2 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 1 |  | 2 | NOTES 1,2,3
IO SIGNALS SUMMERY COUNT(TO/FROM GCS-ESD) SHALL BE CONSIDERED IN GCS-ESD SYSTEM I/O COUNT( INCLUDED IN OTHER WORK PACK)
| ITEM |  | I/O TYPE |  | IS/NIS | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 |  | AI-IS-R |  | IS | R |  | ANALOGUE INPUT HARDWARE SIGNAL (INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 3 |  | 4 | NOTES 1,2,3
| 2 |  | DI-NIS-R |  | NIS | R |  | DIGITAL INPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 2 |  | 3 | NOTES 1,2,3
| 3 |  | DO-NIS-R |  | NIS | R |  | DIGITAL OUTPUT HARDWARE SIGNAL (NON INTRINSICALLY SAFE, REDUNDANT) | [6 empty] | 1 |  | 2 | NOTES 1,2,3
DIGITAL DI-DO (To SIAHMAKAN) SUMMERY COUNT
| ITEM |  | DIGITAL INPUT /OUTPUT |  |  | R/NR |  | DESCRIPTION | [6 empty] | QTY OF SIGNALS |  | QTY (+20% SPARE) | REMARKS
| 1 |  | DIGITAL INPUT |  |  | R |  | DIGITAL INPUT HARDWARE SIGNAL ( REDUNDANT)( VIA SIL 3 SAFETY RELAY) | [6 empty] | 2 |  | 3 | NOTE 3
| 2 |  | DIGITAL OUTPUT |  |  | R |  | DIGITAL INPUT HARDWARE SIGNAL ( NON-REDUNDANT)( VIA SIL 3 SAFETY RELAY) | [6 empty] | 2 |  | 3 | NOTE 3
ABBREVIATIONS:
|  | I/O |  | INPUT / OUTPUT | [7 empty] | DCS: | DISTRIBUTED CONTROL SYSTEM
|  | DI: |  | DIGITAL INPUT SIGNAL | [7 empty] | ESD: | EMERGENCY SHUT DOWN SYSTEM
|  | DO: |  | DIGITAL OUTPUT SIGNAL | [7 empty] | F&G | FIRE AND GAS CONTROL SYSTEM
|  | AI: |  | ANALOGUE INPUT SIGNAL | [7 empty] | MCC: | MOTOR CONTROL CENTER
|  | AO: |  | ANALOGUE OUTPUT SIGNAL | [7 empty] | IRP: | INTERPOSING RELAY PANEL
|  | IND: |  | INDICATION | [7 empty] | CH: | CHANNEL
|  | STA: |  | STATUS | [7 empty] | ADD: | ADDRESS
|  | COM: |  | COMMAND | [7 empty] | TB: | TERMINAL BLOCK
|  | IS |  | INTRINSICALLY SAFE | [7 empty] | R: | REDUNDANT
|  | NIS |  | NON INTRINSICALLY SAFE | [7 empty] | NR: | NON-REDUNDANT

## IO Signals (To GCS)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL /ESD SYSTEM
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK | PPL | PEDCO | 320 |  | IN |  | LI |  | 0002 |  |  | D00
I/O List for ESD/DCS OF GCS
ITEM | TAG | DESCRIPTION | SERVICE |  | P&ID |  |  | I/O TYPE |  | FROM |  | TO |  | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | FUNCTION |  | REMARK | REV.
[14 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL | IND/STA | COM.
1 | DS-3201 | Door Limit Switch | PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  | See Note 4 In Below Page | D00
2 | ZS-3201 | Pig Signaler | PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  |  | DI-NIS-NR |  | FIELD |  | DCS |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  | See Note 4 In Below Page | D00
3 | PSOV-3201 | Solenoid Valve | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  |  | DO-NIS-NR |  | DCS |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X | See Note 4 In Below Page | D00
4 | EZSC-3201 | Emergency shutdown Limit Switch Close | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  | See Note 4 In Below Page | D00
5 | EZSO-3201 | Emergency shutdown Limit Switch Open | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  |  | DI-NIS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  | See Note 4 In Below Page | D00
6 | ESOV-3201 | Solenoid Valve | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  |  | DO-NIS-R |  | ESD |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X | See Note 4 In Below Page | D00
7 | PIT-3201A | Pressure Indicator Transmitter | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  | See Note 4 In Below Page | D00
8 | PIT-3201B | Pressure Indicator Transmitter | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  | See Note 4 In Below Page | D00
9 | PIT-3201C | Pressure Indicator Transmitter | From DEHYDRATION (PK-2101) To PL-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) |  |  | AI-IS-R |  | FIELD |  | ESD |  | * | * | * | * | * | * | * | * |  |  |  | X | X |  | See Note 4 In Below Page | D00
10
11
12
13
14
15
16
17
18
19
20
NOTE 4 : ALL I/O's EXISTING IN THIS PAGE SHALL BE CONSIDERED IN ESD AND DCS SYSTEM OF GCS WORKPACKAGE IN BINAK.

## DIGITAL DI-DO (To Siahmakan)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
I/O LIST FOR CONTROL /ESD SYSTEM
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
9184 – 073 - 053 |  |  |  | BK | PPL | PEDCO | 320 |  | IN |  | LI |  | 0002 |  |  | D00
CONVENTIONAL RELAY BASED DIGITAL SIGNAL FOR EXISTING COMMON CONTROL/ESD SYSTEM OF SIAHMAKAN
ITEM | TAG | DESCRIPTION | SERVICE |  | P&ID |  |  | SIGNAL TYPE |  | FROM |  | TO |  | SYSTEM CABINET |  |  |  |  | Marshalling Cabinet |  |  | ALARM |  |  |  | FUNCTION |  | REMARK | REV.
[14 empty] | CABINET NO. | RACK | SLOT | CH. | ADD. | CABINET NO. | TB NO. | ADD. | HH | H | L | LL | IND/STA | COM.
3 | PSOV-3202 | Solenoid Valve | PR-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  |  | Digital Output (Note 5 in Below Page) |  | Note 6 in Below Page |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X | SEE NOTES 1,2 IN BELOW PAGE | D00
4 | EZSC-3202 | Emergency shutdown Limit Switch Close | PR-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  |  | Digital Input (Note 5 in Below Page) |  | FIELD |  | Note 6 in Below Page |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  | SEE NOTES 1,2 IN BELOW PAGE | D00
5 | EZSO-3202 | Emergency shutdown Limit Switch Open | PR-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  |  | Digital Input (Note 5 in Below Page) |  | FIELD |  | Note 6 in Below Page |  | * | * | * | * | * | * | * | * |  |  |  |  | X |  | SEE NOTES 1,2 IN BELOW PAGE | D00
6 | ESOV-3202 | Solenoid Valve | PR-3201 |  | BK-PPL-PEDCO-320-PR-PI-0001 (3/3) |  |  | Digital Output (Note 5 in Below Page) |  | Note 6 in Below Page |  | FIELD |  | * | * | * | * | * | * | * | * | [5 empty] | X | SEE NOTES 1,2 IN BELOW PAGE | D00
54
55
56
68
69
70
68
69
70
68
69
70
68
69
70
68
69
70
NOTE 5: THIS SIGNAL IS CONVENTIONAL RELAY BASED.
NOTE 6: ALL INPUT/OUTPUT SIGNALS FOR ABOVE ITEMS SHALL BE CONNECTED TO EXISTING CONVENTIONAL RELAY BASED CONTROL /ESD SYSTEM OF SIAHMAKAN PLANT. REDUNDANT RELAY BASED SHALL BE CONSIDERED FOR ESD SIGNALS ALSO ONE COMMON JUNCTION BOX AND ONE COMMON MULTI CORE WILL BE USED FOR THIS SIGNALS.