## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 18
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | IN | DT | 0011 | D00
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR CONTROL/REGULATOR VALVES نگهداشت و افزایش تولید میدان نفتی بینک
D00 |  | JUN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-708932
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 18
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | IN | DT | 0011 |  | D00
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | [7 empty] | 65
2 | X | [7 empty] | 66
3 | X | [7 empty] | 67
4 | X | [7 empty] | 68
5 | X | [7 empty] | 69
6 | X | [7 empty] | 70
7 | X | [7 empty] | 71
8 | X | [7 empty] | 72
9 | X | [7 empty] | 73
10 | X | [7 empty] | 74
11 | X | [7 empty] | 75
12 | X | [7 empty] | 76
13 | X | [7 empty] | 77
14 | X | [7 empty] | 78
15 | X | [7 empty] | 79
16 | X | [7 empty] | 80
17 | X | [7 empty] | 81
18 | X | [7 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## REFERENCE
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 18
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | IN | DT | 0011 | D00
REFERENCE DOCUMENTS :
|  | Specification For Instrumentation | [6 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001_D00
|  | Process Basis Of Design | [6 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001_D05
|  | Piping Material Specification | [6 empty] | BK-GCS-PEDCO-120-PI-SP-0001_D01
|  | Symbol & Legend For PFD and P&ID | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0001_D02
|  | P&ID - Gas Compression Inlet Gas Pipeline (Binak) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0002_D03
|  | P&ID - Gas Compression Inlet Gas Pipeline (Golkhari) | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0003_D03
|  | P&ID - Slug Catcher System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0004_D03
|  | P&ID - Gas Compression Inlet Knock Out Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0005_D03
|  | P&ID - 1st Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0006_D03
|  | P&ID - 1st Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0007_D03
|  | P&ID - 1st Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0008_D03
|  | P&ID - 2nd Stage Gas Compression Suction Drums | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0009_D03
|  | P&ID - 2nd Stage Gas Compression Compressors | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0010_D03
|  | P&ID - 2nd Stage Gas Compression Air Coolers | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0011_D03
|  | P&ID - 2nd Stage Gas Compression Discharge Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0012_D03
|  | P&ID - Gas Compression Dehydration Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0013_D03
|  | P&ID - Lean Glycol Storage Tank | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0014_D03
|  | P&ID - Instrument & Plant Air System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0015_D03
|  | P&ID - Nitrogen Generation System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0016_D03
|  | P&ID - Close Drain System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0017_D03
|  | P&ID - Corrosion Inhibitor Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0018_D03
|  | P&ID - Methanol Injection Package | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0019_D03
|  | P&ID - LP Flare System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0020_D03
|  | P&ID - Oily Water Sewer | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0021_D03
|  | P&ID - Fuel Gas System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0022_D03
|  | P&ID - Diesel Oil System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0023_D03
|  | P&ID - Potable Water System | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0024_D03
|  | P&ID - Glycol Sump Drum | [6 empty] | BK-GCS-PEDCO-120-PR-PI-0025_D03
|  | P&ID - Fire Water Network | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0001_D00
|  | P&ID - Total Flooding System For Extension of Existing Elect. Building | [6 empty] | BK-GCS-PEDCO-120-SA-PI-0002_D01

## Notes
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 18
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | IN | DT | 0011 | D00
GENERAL NOTES:
1-The electrical equipment shall be suitable for hazardous area gas group IIB, temperature class T4.
2-Flow direction shall be specified on the valve body.
3- All flanges shall be in accordance with ASME B16.5.
4- Each valve shall be furnished with name plate as per "specification for control valves" with No. "BK-GNRAL-PEDCO-000-IN-SP-0002 ".
5- The following items shall be considered:
- Design standard for globe valves: ips-m-in-160, bs1873
- Design standard for plug valves: ips-m-in-160 api 599
- Valve bonnet and bottom flanges shall be of botled construction with fully retained gaskets
- Trim and seat shall be easily replaceable. seat should be damped or backed up by a seat retainer
- Packing material / packing construction: teflon/chevron type
- Material test certificate
- Dimentional check
- Hydrostatic test
- Performance and mechanical operation test
- Testy certificate including pressure test, visual, dimentional and nude
- Seal leakage test
- Casting examination for valves 6 inches and larger in class 600 and higher as per ansi b 16.34
- Casting quality valves shall ndt(rt tested)
- Mill test certificate for all metallic parts
6- Screwed bolt-type limit stops, e.g. on the control valve stem, adjustable over the full length of the stroke shall be applied. the vendor shall set
7- 2 Nos. Eye-Bolt and 2 Nos. Jack Bolt for each valve to be supplied by vendor.
8 - Environmental condition for field instrumentation of Binak Oilfield shall be considered as per the followings:
| • Minimum winter dry bulb: 0.0 °C • Maximum winter relative humidity: 100 • Buildings heating, design dry bulb: 6.0 °C • Design winter dry bulb: -1.0 °C • Design winter relative humidity: 100% • Maximum summer dry bulb: 50.26°C • Maximum summer relative humidity: 100% • Buildings cooling, design dry bulb: 41.0 °C |  |  |  |  | • Design summer dry bulb: 77.0 °C • Maximum sun temperature: 85.0 °C • Maximum Shade Temperature: 52.0 °C • Minimum Design relative humidity: 0 • Min. average ambient temperature (°C): 8.35 °C • Max. Average ambient temperature (°C): 35 °C • Min .Absolut air temperature(°C): 0 °C • Max .Absolut air temperature(°C): 47.09 °C
Relative Humidity:
• Maximum Range: 92.27% • Average Relative Humidity 54.7% • Minimum Relative Humidity: 34.94%

## FCV-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 5 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | FCV-2101
|  |  | 2 | Service | [10 empty] | Gas Compression Inlet Gas Pipeline (Binak)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0001-AN07-6"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0002
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AN07 | [7 empty] | SCH.80
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 6" | [7 empty] | ASTM A106 Gr.B , B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 9
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 7220.492 |  |  | 6564.084 |  |  |  | 1521.413
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 6.5 |  |  | 6.5 |  |  |  | 6.5
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 1 |  |  | 1 |  |  |  | 1
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 46.11 |  |  | 46.11 |  |  |  | 46.11
|  |  | 18 | Liquid/ GAS Specific Gravity (Gl) | [15 empty] | 0.23
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.9704
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.011
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.225
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 141.7
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 106.1
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 109.24 |  |  | 99.28 |  |  |  | 22.97
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 61.1 |  |  | 55.3
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 6" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 6" # 150 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## FCV-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 6 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | FCV-2102
|  |  | 2 | Service | [10 empty] | Gas Compression Inlet Gas Pipeline (Golkhari)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0012-AN07-8"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0003
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AN07 | [7 empty] | SCH.60
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 8" | [7 empty] | ASTM A106 Gr.B , B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 9
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 12395.931 |  |  | 11269.028 |  |  |  | 3181.682
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 6.5 |  |  | 6.5 |  |  |  | 6.5
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 1 |  |  | 1 |  |  |  | 1
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 32 |  |  | 32 |  |  |  | 32
|  |  | 18 | Liquid/ GAS Specific Gravity (Gl) | [15 empty] | 0.214
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.973
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.011
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.261
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 182.7
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 102.1
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 194.79 |  |  | 176.97 |  |  |  | 49.77
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 63.5 |  |  | 57.4
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 6" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 6" # 300 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## FCV-2111
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 7 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | FCV-2111
|  |  | 2 | Service | [10 empty] | Slug Catcher System
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CDH-112-0014-CN05-3"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0004 (2 of 2)
|  |  | 4 | Area Classification | [10 empty] | Zone1, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | CN05 | [7 empty] | SCH.40
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 3" | [7 empty] | ASTM A106 Gr.B , B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 5.5
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 7854.443 |  |  | 7140.403 |  |  |  | 2142.121
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 19 |  |  | 19 |  |  |  | 19
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 1 |  |  | 1 |  |  |  | 1
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 24.22 |  |  | 24.22 |  |  |  | 24.22
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | 0.716
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | -
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.63
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.224
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 1.788
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 75.73
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 10.75 |  |  | 9.77 |  |  |  | 2.93
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 55.7 |  |  | 50.3
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 1.5" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 1.5" # 300 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | ASTM A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## LCV-2114
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 8 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | LCV-2114
|  |  | 2 | Service | [10 empty] | Gas Compression Inlet Knock Out Drum to Closed Drain
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | CDH-111-0019-AS00-2"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0005
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | NOT Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AS00 | [7 empty] | SCH.10S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | NP / 2" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P | [10 empty] | 14.5
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | XXX |  |  | XXX |  |  |  | 4.58
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | XXX
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | XXX
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | XXX
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | XXX
|  |  | 22 | Vapour Pressure | [10 empty] | bar-a |  |  |  |  | XXX
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-a
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 85.9 |  |  | XXX |  |  |  | XXX
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | X" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | X" # 300 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2123A
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 9 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2123A
|  |  | 2 | Service | [10 empty] | 1st Stage Gas Compression Suction Drums (C-2101A)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0045A-FS00-6"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0006 (1 of 3)
|  |  | 4 | Area Classification | [10 empty] | Zone 2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Not Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FS00 | [7 empty] | SCH.40S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | NP / 6" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P | [10 empty] | 14.5
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | XXX |  |  | XXX |  |  |  | 4.58
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | XXX
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | XXX
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | XXX
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | XXX
|  |  | 22 | Vapour Pressure | [10 empty] | bar-a |  |  |  |  | XXX
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-a
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 85.9 |  |  | XXX |  |  |  | XXX
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | X" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | X" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2123B
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 10 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2123B
|  |  | 2 | Service | [10 empty] | 1st Stage Gas Compression Suction Drums (C-2101B)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0045B-FS00-6"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0006 (2 of 3)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Not Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FS00 | [7 empty] | SCH.40S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | NP / 6" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P | [10 empty] | 14.5
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | XXX |  |  | XXX |  |  |  | 4.58
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | XXX
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | XXX
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | XXX
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | XXX
|  |  | 22 | Vapour Pressure | [10 empty] | bar-a |  |  |  |  | XXX
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-a
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 85.9 |  |  | XXX |  |  |  | XXX
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | X" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | X" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2123C
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 11 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2123C
|  |  | 2 | Service | [10 empty] | 1st Stage Gas Compression Suction Drums (C-2101C)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0045C-FS00-6"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0006 (3 of 3)
|  |  | 4 | Area Classification | [10 empty] | Zone 2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Not Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FS00 | [7 empty] | SCH.40S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | NP / 6" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P | [10 empty] | 14.5
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | XXX |  |  | XXX |  |  |  | 4.58
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | XXX
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | XXX
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | XXX
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | XXX
|  |  | 22 | Vapour Pressure | [10 empty] | bar-a |  |  |  |  | XXX
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-a
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | XXX |  |  | XXX |  |  |  | XXX
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 85.9 |  |  | XXX |  |  |  | XXX
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | X" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | X" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2135A
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 12 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2135A
|  |  | 2 | Service | [10 empty] | 2nd Stage Gas Compression Air Coolers (C-2102A)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0057A-FS00-4"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011 (1 of 3)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Not Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FS00 | [7 empty] | SCH.40S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | NP / 4" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 62
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 9530.038 |  |  | 8663.671 |  |  |  | 2275.632
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 54.1 |  |  | 54.1 |  |  |  | 54.1
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 52.6 |  |  | 52.6 |  |  |  | 52.6
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 60 |  |  | 60 |  |  |  | 60
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | 0.059
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.82/0.036
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.014
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.457
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 168.1
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 93.65
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 10.12 |  |  | 9.17 |  |  |  | 2.36
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 60.5 |  |  | 54.5
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 2" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 2" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2135B
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 13 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2135B
|  |  | 2 | Service | [10 empty] | 2nd Stage Gas Compression Air Coolers (C-2102B)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0057B-FS00-4"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011 (2 of 3)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Not Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FS00 | [7 empty] | SCH.40S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | NP / 4" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 62
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 9530.038 |  |  | 8663.671 |  |  |  | 2275.632
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 54.1 |  |  | 54.1 |  |  |  | 54.1
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 52.6 |  |  | 52.6 |  |  |  | 52.6
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 60 |  |  | 60 |  |  |  | 60
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | 0.059
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.82/0.036
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.014
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.457
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 168.1
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 93.65
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 10.12 |  |  | 9.17 |  |  |  | 2.36
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 60.5 |  |  | 54.5
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 2" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 2" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2135C
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 14 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2135C
|  |  | 2 | Service | [10 empty] | 2nd Stage Gas Compression Air Coolers (C-2102C)
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0057C-FS00-4"-NP | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0011 (3 of 3)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Not Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FS00 | [7 empty] | SCH.40S
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | NP / 4" | [7 empty] | ASTM A312 TP 316L , B36.19M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 62
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 9530.038 |  |  | 8663.671 |  |  |  | 2275.632
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 54.1 |  |  | 54.1 |  |  |  | 54.1
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 52.6 |  |  | 52.6 |  |  |  | 52.6
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 60 |  |  | 60 |  |  |  | 60
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | 0.059
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.82/0.036
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.014
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.457
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 168.1
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 93.65
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 10.12 |  |  | 9.17 |  |  |  | 2.36
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 60.5 |  |  | 54.5
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 2" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 2" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A351 GR. CF3M | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2151
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 15 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2151
|  |  | 2 | Service | [10 empty] | Gas Compression Dehydration Package
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | GAS-111-0072-FN05-6"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH.80
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 6" | [7 empty] | ASTM A106 Gr.B , ASME B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 5.5
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 18887.886 |  |  | 17170.805 |  |  |  | 4531.569
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 51.9 |  |  | 51.9 |  |  |  | 51.9
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 1 |  |  | 1 |  |  |  | 1
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 59.42 |  |  | 59.42 |  |  |  | 59.42
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | 0.552
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.8292
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.013
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.448
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 104.9
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 93.45 |  |  | 84.95 |  |  |  | 22.4
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 72.4 |  |  | 65.5
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 4" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 4" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2152
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 16 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2152
|  |  | 2 | Service | [10 empty] | Gas Compression Dehydration Package
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | FL-112-0029-AN07-4"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0013 (1 of 3)
|  |  | 4 | Area Classification | [10 empty] | Zone 2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | FN05 | [7 empty] | SCH.80
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 4" | [7 empty] | ASTM A106 Gr.B , ASME B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 62
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 18887.886 |  |  | 17170.805 |  |  |  | 4292.701
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 52.9 |  |  | 52.9 |  |  |  | 52.9
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 50.9 |  |  | 50.9 |  |  |  | 50.9
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 59.422 |  |  | 59.422 |  |  |  | 59.422
|  |  | 18 | Liquid Specific Gravity (Gl) | [15 empty] | 0.552
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.8292
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.013
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.448
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | -
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 104.9
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 21.36 |  |  | 19.37 |  |  |  | 4.75
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 63.4 |  |  | 57.2 |  |  |  | 12.1
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 3" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 3" # 600 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2201
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 17 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2201
|  |  | 2 | Service | [10 empty] | Instrument & Plant Air System
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | PLA-112-0010-AN04-1 1/2"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0015 (1 of 2)
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | NOT Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AN04 | [7 empty] | SCH.80
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 1 1/2" | [7 empty] | ASTM A106 Gr.B , ASME B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 12.5
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 42.623 |  |  | 38.748 |  |  |  | 11.624
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 9 |  |  | 9 |  |  |  | 9
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 4.5 |  |  | 4.5 |  |  |  | 4.5
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 65 |  |  | 65 |  |  |  | 65
|  |  | 18 | GAS Specific Gravity (Gl) | [15 empty] | 0.196
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.98
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.012
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.229
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 168.1
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 93.65
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 0.3 |  |  | 0.27 |  |  |  | 0.08
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 72.8 |  |  | 67.9 |  |  |  | 25.6
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 1" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 1" # 800 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | ASTM A 105 | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.

## PCV-2272
نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR CONTROL/REGULATOR VALVES
شماره پیمان: | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه | 18 |  | از |  | 18 |  | شماره صفحه :
9038 – 073 - 053 | [5 empty] | BK |  | GCS |  | PEDCO |  | 120 |  | IN |  | DT |  | 0011 |  |  | D00
DATA SHEETS FOR CONTROL/REGULATOR VALVES
GENERAL |  |  | 1 | Tag No. | [10 empty] | PCV-2272
|  |  | 2 | Service | [10 empty] | From Inlet K.O. Drum to V-2205
|  |  | 3 | Line No. | [6 empty] | P&ID No. |  |  |  | FLG-112-0040-AN07-2"-PT | [7 empty] | BK-GCS-PEDCO-120-PR-PI-0022
|  |  | 4 | Area Classification | [10 empty] | Zone2, IIB T4
|  |  | 5 | Ambient Temperature | [5 empty] | ⁰C | Min. |  | Max. |  | 5 | [7 empty] | 50
|  |  | 6 | Available Air Supply Pressure |  |  |  |  | barg |  | Min. |  | Max. |  | 3 | [7 empty] | 8
|  |  | 7 | Nace Requirement: | [10 empty] | NOT Required
PIPE & LINE |  |  | 8 | Pipe Class | [6 empty] | Pipe Sch. |  |  |  | AN07 | [7 empty] | SCH.160
|  |  | 9 | Pipe Line Insulation ¦Line Size | [6 empty] | Pipe Material |  |  |  | PT / 2" | [7 empty] | ASTM A106 Gr.B , ASME B36.10M
PROCESS CONDITIONS |  |  | 10 | Fluid | [10 empty] | Gas
|  |  | 11 | State | [10 empty] | Gas
|  |  | 12 | Shut Off Pressure delta P ( BARG) | [10 empty] | 9
|  |  | 13 | [11 empty] | Units |  |  |  |  | Max |  |  | Norm. |  |  |  | Min.
|  |  | 14 | Flow Rate(vapor/water/oil) | [10 empty] | kg/h |  |  |  |  | 556.347 |  |  | 505.77 |  |  |  | 151.731
|  |  | 15 | Inlet Pressure | [10 empty] | bar-g |  |  |  |  | 5.1 |  |  | 5.1 |  |  |  | 5.1
|  |  | 16 | Pressure Drop | [10 empty] | bar |  |  |  |  | 0.2 |  |  | 0.2 |  |  |  | 0.2
|  |  | 17 | Inlet Temperature(max) | [10 empty] | ⁰C |  |  |  |  | 36.921 |  |  | 36.921 |  |  |  | 36.921
|  |  | 18 | GAS Specific Gravity (Gl) | [15 empty] | 0.199
|  |  | 19 | Compressibility Factor(Z)(vapour/water/oil) | [10 empty] | - |  |  |  |  | 0.975
|  |  | 20 | Viscosity (vapour/water/oil) | [10 empty] | cP |  |  |  |  | 0.011
|  |  | 21 | Specific Heats Ratio(Cp/Cv) (vapour/liquid) | [12 empty] | - |  |  | 1.245
|  |  | 22 | Vapour Pressure | [10 empty] | bar-g |  |  |  |  | 168.1
|  |  | 23 | Critical Pressure (liquid) | [10 empty] | bar-g |  |  |  |  | 93.65
CALCULATED RESULTS |  |  | 24 | Flow Coefficient Cv | [10 empty] | - |  |  |  |  | 18.9 |  |  | 17.18 |  |  |  | 5.15
|  |  | 25 | Travel | [10 empty] | % |  |  |  |  | 83.3 |  |  | 75.5
|  |  | 26 | Sound Pressure Level | [10 empty] | dBA |  |  |  |  | MAX 85 dBA(VTC) |  |  | MAX 85 dBA(VTC) |  |  |  | MAX 85 dBA(VTC)
BODY AND TRIM |  |  | 27 | Body size |  |  |  | 1" (VTC) | [6 empty] | POSITIONER |  |  |  | 50 | Type |  |  |  |  | Electrical-Pneumatic(SMART)
|  |  | 28 | Rated Cv |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 51 | Input Signal |  |  |  |  | 4~20 mA-Hart
|  |  | 29 | End conn. & Rating |  |  |  | 1" # 150 | [10 empty] | 52 | Power Supply |  |  |  |  | 24 VDC loop powered
|  |  | 30 | Body/Bonnet Material |  |  |  | A216 GR. WCB | [10 empty] | 53 | Electrical Connection |  |  |  |  | ISO M20 x 1.5
[19 empty] | 54 | Direct/Reverse Act. |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 31 | Body/Bonnet Type |  |  |  | GLOBE / Bolted Flange Bonnet | [10 empty] | 55 | Lock Last Position |  |  |  |  | (NOTE 4 in Below Table)
|  |  | 32 | Flow Direction |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 56 | Output Signal |  |  |  |  | 3-15 Psi
|  |  | 33 | Packing Material |  |  |  | P.T.F.E. | [10 empty] | 57 | I.P./Ex.Protec. |  | Gauge |  |  | IP65 / EExia |  |  | Yes
|  |  | 34 | Trim Type |  |  |  | SINGLE SEATED/CAGE | [10 empty] | 58 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 35 | Characteristic |  |  |  | EQUAL PERCENTAGE (VTC) | [6 empty] | SOLENOID VALVE |  |  |  | 59 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 36 | Guiding |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 60 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 37 | Rated Travel |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 61 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
|  |  | 38 | Plug/Disk Material |  |  |  | SS316 | [10 empty] | 62 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 39 | Seat Material |  |  |  | SS316 | [6 empty] | SWITCHES |  |  |  | 63 | Type |  | Qty. |  |  | N/A |  |  | N/A
|  |  | 40 | Cage/Guid Material |  |  |  | SS316 | [10 empty] | 64 | Power Supply |  |  |  |  | N/A
|  |  | 41 | Stem Material |  |  |  | SS316 | [10 empty] | 65 | Contacts / Rating |  |  |  |  | N/A
|  |  | 42 | Trim Material |  |  |  | SS316 | [10 empty] | 66 | Switching Position |  |  |  |  | N/A
|  |  | 43 | MFR | Model |  |  | (NOTE 4 in Below Table) | [10 empty] | 67 | I.P. |  | Ex.Protec. |  |  | N/A |  |  | N/A
ACTUTOR |  |  | 44 | Size | Eff.Area |  |  | (NOTE 4 in Below Table) | [10 empty] | 68 | MFR |  | Model |  |  | N/A |  |  | N/A
|  |  | 45 | Air Failure | Handwheel |  |  | FAIL CLOSE |  |  | SIDE MOUNTED |  |  |  | AIR SET |  |  |  | 69 | Set Pressure |  |  |  |  | Yes
|  |  | 46 | Air Action | Orientation |  |  | AIR TO OPEN |  |  | VERT. UP | [7 empty] | 70 | Filter |  | Gauge |  |  | Yes |  |  | Yes
|  |  | 47 | Actuator Type |  |  |  | Pneumatic Diaphragm Actuators | [10 empty] | 71 | Pnumatic Conn. |  |  |  |  | 1/4 " NPTF
|  |  | 48 | AIR Press. | Min/ Max/ Des. |  | (Barg) | 4 (Note 3 in Below Table) |  |  | 7.5 |  | 8.5 | [5 empty] | 72 | MFR |  | Model |  |  | (NOTE 4 in Below Table)
|  |  | 49 | MFR | Model |  |  | (NOTE 4 in Below Table) | [6 empty] | TESTS |  |  |  | 73 | Hydro. Pressure |  |  |  |  | API 598
[19 empty] | 74 | Leakage Class |  |  |  |  | ANSI IV
[19 empty] | 75 | Performance Test |  |  |  |  | Required
[15 empty] | OPTIONS |  |  |  | 76 | Internal Tubing |  |  |  |  | Required(with Double Ferrule Compression conn.)
[19 empty] | 77 | Tube Material |  |  |  |  | 316 S.S
PURCHASE |  |  | Manufacturer |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 78 | Cable Gland |  |  |  |  | M20, Nickel plated brass
|  |  | Model |  |  |  |  | (NOTE 4 in Below Table) | [10 empty] | 79 | Cable Entry |  |  |  |  | M20 X 1.5
NOTES:
1- All materials shall be in accordance with 'Piping Material Specification' ,Document No.: .BK-GCS-PEDCO-120-PI-SP-0001
2- VTA: Vendor To Advise VTC: Vendor To Confirm
3- Minimmum of instrument air pressure supply is 4 barg but 3 barg as minimmum working pressure, shall be considered for actuator sizing .
4- Shall be stated by vendor at quotaion stage.