## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 6
9184 – 073 - 053 |  |  | BK |  | PPL | PEDCO | 320 |  | IN | DT | 0003 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | JUN.2022 |  | IFA |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | JAN.2022 |  | IFC |  |  |  | P.Hajisadeghi |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F9Z-708583
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 6
9184 – 073 - 053 |  |  | BK | PPL |  | PEDCO | 320 | IN | DT | 0003 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 65
2 | X | X | [6 empty] | 66
3 | X | X | [6 empty] | 67
4 | X | X | [6 empty] | 68
5 | X | X | [6 empty] | 69
6 | X | X | [6 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## Reference
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 6
9184 – 073 - 053 |  |  | BK | PPL | PEDCO | 320 | IN |  | DT | 0003 | D01
REFERENCE DOCUMENTS :
|  | 1.Instrument & Control System Design Criteria | [5 empty] | BK-PPL-PEDCO-320-IN-DC-0001_D00
|  | 2.P&ID - Gas Pipeline (to Siahmakan G.I. Station) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0001_D02
|  | 3.P&ID - Condensate Pipeline (to Binak PU) | [5 empty] | BK-PPL-PEDCO-320-PR-PI-0002_D02
|  | 4.Piping Material Specification | [5 empty] | BK-PPL-PEDCO-320-PI-SP-0001_D01
|  | 5.Specification For Instrumentation | [5 empty] | BK-GNRAL-PEDCO-000-IN-SP-0001_D03
|  | 6. Instrument Hook-Up Diagram | [5 empty] | BK-PPL-PEDCO-320-IN-DG-0002_D00
|  | 7. Process Basic of Design | [5 empty] | BK-GNRAL-PEDCO-000-PR-DB-0001_D01
D01

## General Notes
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 6
9184 – 073 - 053 |  |  |  | BK | PPL | PEDCO | 320 | IN | DT | 0003 | D01
GENERAL NOTES:
1 - Zero and span adjustment shall be included and be accessible from outside in addition to Hand Held Communicator (HHC).
2 - Pressure elements shall be furnished with over-range protection to at least 1.5 times the maximum range of the instrument
3 - S.S. name plate including project description to be provided.
4 - Painting shall be in accordance with manufacturer standard.
5- If smart type transmitters are selected for ESD application they shall be configured as “write protected”.
6- All instruments and micro-processor based system shall meet the following Radio Frequency Immunity (RFI) requirements that shall be tested at the acceptance test stage. Basic reference standard is IEC 60801 (part 3) for design and manufacturing considerations.
7-Tropicalization shall be applied to protect electrical circuits and electronic cards from being degraded by corrosion and/or fungus growth.
8- Environmental condition for field instrumentation of BINAK Complex shall be considered as per the followings:
Maximum ambient temperature: 50 (°C)
Minimum ambient temperature: 5 (°C)
Maximum steel surface exposed to sun: 85 (°C)
Maximum summer dry bulb: 50 (°C)
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
Maximum Design relative humidity (%): 100
Minimum Design relative humidity (%): 0
9- Material Test Certificate and calibration Certificate for all transmitters to be submitted by Vendor.
D01

## PT
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه | شماره صفحه: 5 از 6
9184 – 073 - 053 |  |  |  | BK | PPL |  | PEDCO | 320 | IN | DT |  | 0003 | D01
PRESSURE TRANSMITTER
| GENERAL DATA | 1 | Tag No. | [7 empty] | SEE NEXT PAGE
|  | 2 | P&ID No. | [7 empty] | SEE NEXT PAGE
|  | 3 | Equipment No. / Line No. | [7 empty] | SEE NEXT PAGE
|  | 4 | Area Classification | [7 empty] | ZONE 2, IIB T4
|  | 5 | Piping Class | [7 empty] | SEE NEXT PAGE
| OPERATING CONDITIONS | 6 | Fluid | [7 empty] | SEE NEXT PAGE
|  | 7 | Phase | [7 empty] | SEE NEXT PAGE
|  | 8 | Operating Pressure | [5 empty] | (bar-g) |  | SEE NEXT PAGE
|  | 9 | Design Pressure | [5 empty] | (bar-g) |  | SEE NEXT PAGE
|  | 80 | Operating Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
|  | 11 | Design Temperature | [5 empty] | (°C) |  | SEE NEXT PAGE
| TRANSMITTER | 12 | Element Type |  |  |  | (NOTE 4 IN BELOW TABLE) |  |  |  | SEE NEXT PAGE
|  | 13 | Size of Process Connection | [7 empty] | SEE NEXT PAGE
|  | 14 | Rating of Process Connection | [7 empty] | SEE NEXT PAGE
|  | 15 | Element Material | [7 empty] | SEE NEXT PAGE
|  | 16 | Enclosure Material | [7 empty] | Die cast aluminium
|  | 17 | Instrument Range | [7 empty] | SEE NEXT PAGE
|  | 18 | Calibration Range | [7 empty] | SEE NEXT PAGE
|  | 19 | Power Supply | [7 empty] | 24 VDC-Loop powered
|  | 20 | Output Signal | [7 empty] | 4-20mA
|  | 21 | Communication Protocol | [7 empty] | HART(4-20mA)
|  | 22 | Electrical Connection | [7 empty] | ISO M20 x 1.5
|  | 23 | Electrical Certification | [7 empty] | EEx "ia"
|  | 24 | Weather Protection | [7 empty] | IP-65 as minimum
|  | 25 | Accuracy | [7 empty] | +/- 0.1% F.S
|  | 26 | Repetability | [7 empty] | +/- 0.1% F.S
|  | 27 | Span and Zero Adjustment | [7 empty] | Required
|  | 28 | Over Range Protection | [7 empty] | Yes/ 1.5 Times the Maximum Range (Note 2 in General note)
|  | 29 | Write Protected | [7 empty] | Required (see Note 5 in General Note)
|  | 30 | RFI Protection | [7 empty] | Required (see Note 6 in General Note)
|  | 31 | Tropicalization | [7 empty] | Required (see Note 7 in General Note)
| DIAPHRAGM SEAL | 32 | Type | [7 empty] | N/A
|  | 33 | Size (In) | [7 empty] | N/A
|  | 34 | Fill Fluid | [7 empty] | N/A
|  | 35 | Diaphragm Material | [7 empty] | N/A
|  | 36 | Capillary Material | [7 empty] | N/A
|  | 37 | Capillary Length | [7 empty] | N/A
| OPTIONS | 38 | Integral Indicator |  |  |  | Display Unit |  |  |  | Required |  |  |  |  | Bar-g
|  | 39 | Mounting Brackets | [7 empty] | Required, 2" Support Pipe (Note 3 In Below Table)
|  | 40 | Manifold |  |  |  | Manifold Material |  |  |  | 2 Way Block & Bleed Manifold |  |  |  |  | 316 S.S
|  | 41 | Connection | [7 empty] | 1/2 " NPT (Note 2,5,7 in below table)
|  | 42 | Manifold Model |  |  |  | Manifold Manufacturer |  |  |  | will be finalized
|  | 43 | Integral Indicator Style | [7 empty] | LCD TYPE
|  | 44 | NACE Requirements | [7 empty] | SEE NEXT PAGE
| PURCHASING DATA | 4 5 | Model |  |  |  | Manufacturer |  |  |  | will be finalized |  |  |  | will be finalized
|  | 46 | Supplier |  |  |  | Order |  |  |  | will be finalized |  |  |  | will be finalized
| NOTES : | VTA : VENDOR TO ADVISE |  |  |  | N/A: NOT APPLICABLE |  |  |  | VTC: VENDOR TO CONFIRM
1 : As per specification (reference 5) , all of the wetted parts in Sour service " Specification For Material Requirements in Sour service BK-GNRAL-PEDCO-000-PI-SP-0008" and NACE-MR-0175/ISO 15156 shall be covered where in Piping/Pipeline Material Specification recommended.
2 :All manifolds shall be suitble for connection to transmitter and process line.
3 : Mounting Yoke, U-bolt , Nuts and all accessories shall be supplied by vendor.
4 : Suitble element type to be confirmed by vendor.
5: For manifoled rating, refer to "Piping Material Specification Doc No.BK-PPL-PEDCO-320-PI-SP-0001.
6 :Burn out direction shall be capable to set.
7: Instrument/Process connection to be as belows:
Process Connection:1/2" NPTF
Instrument Connection: 1/2" NPTF
Drain Connection: 1/4" NPTF
8: One "HART COMMUNICATOR DEVICE" shall be provided for Calibrating of the transmitters.
D01

## PT LIST
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک بستههای کاری تحتالارض احداث خطوط انتقال گاز/مایعات گازی از ايستگاه تقويت فشار گاز بينك تا ايستگاه تزريق گاز سياهمكان/واحد بهره برداري بينك
DATA SHEETS FOR PRESSURE / DIFF. PRESSURE TRANSMITTER
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 6 از 6
9184 – 073 - 053 |  |  |  | BK | PPL | PEDCO | 320 | IN |  | DT |  | 0003 |  |  | D01
PRESSURE TRANSMITTER
Rev. | Item No. | Tag No. | P&ID No. | Equipment No. / Line No. | Piping Class/ Rating | Service | Fluid/Phase | Design Pressure (Bar-g) | Operating Pressure (Bar-g) | Design Temp. (°C) | Operating Temp. (°C) | Instrument Range | CalibrationRange (Bar-g) (Note 1) | Element Type | Element Material | Size of Process Connection | Rating of Process Connection | 2 Way Manifold (Block & Bleed) | NACE | Model | Remark
| 1 | PT-3201A | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) | GAS-113-0072-FN05-8"-PT | FN05 | FROM DEHYDRATION (PK-2101) | HYDROCARBON/GAS | 62 | 50.9 | 85 | 58.3 | VTA | 0-100 | Diaphragm (VTC) | SS 316 | 1/2" NPT | See Note 7 In Previous Page | Yes | Yes | VTA | See Note 1 in Below Table
| 2 | PT-3201B | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) | GAS-113-0072-FN05-8"-PT | FN05 | FROM DEHYDRATION (PK-2101) | HYDROCARBON/GAS | 62 | 50.9 | 85 | 58.3 | VTA | 0-100 | Diaphragm (VTC) | SS 316 | 1/2" NPT | See Note 7 In Previous Page | Yes | Yes | VTA | See Note 1 in Below Table
| 3 | PT-3201C | BK-PPL-PEDCO-320-PR-PI-0001 (1/3) | GAS-113-0072-FN05-8"-PT | FN05 | FROM DEHYDRATION (PK-2101) | HYDROCARBON/GAS | 62 | 50.9 | 85 | 58.3 | VTA | 0-100 | Diaphragm (VTC) | SS 316 | 1/2" NPT | See Note 7 In Previous Page | Yes | Yes | VTA | See Note 1 in Below Table
NOTE:
1- Pressure limit valve to be considered by vendor if required (as per project specification and related standards due to vendor selected instrument range)
2- Existing data to be submitted /confirmed by client.
3- For Manifold Pressure Rating (threaded connection), bolt & gasket material refer to "Piping Material Specification DOC NO. BK-PPL-PEDCO-320-PI-SP-0001"
D01