## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-PPL-PEDCO-320-IN-DT-0003_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0587 |  |  | Transmital Date: 13 Feb 2022
Document Title: Data Sheets For Pressure/Diff. Pressure Transmitter |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0011-IN-TR-0587 |  |  | Transmital Date: 13 Feb 2022
[5 empty] | CRS No: PETCO-CRS-BK-PPL-PEDCO-320-IN-DT-0003_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
Instrument Comments
1 | با توجه به اينكه مدرك Area Classification براي unit 320 ارائه نشده است، مورد بايد نهايي گردد. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | این مدرک در حال ارسال می باشد
2 | مواردي مثل piping material، schedule، pipe size، rating ارائه گردد. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | از آنجائیکه مدرک pms در رفرنس 5 قرار دارد بنابراین با توجه کلاس خطی که در مدرک آورده شده است می توان موارد مورد اشاره در آن رفرنس می باشد.
3 | مورد Over Range Protection مجددا بررسي گردد. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | در ردیف 28 مشخص گردید.
4 | متريال Manifold مشخص شود. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | در ردیف 36 مشخص گردید.
5 | با توجه به خورنده بودن سيال و عدم درنظر گرفتن Diaphragm seal ترانسميترهاي فشار Full NACE در نظر گرفته شود. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | از آنجائیکه در basic به دیافراگم سیل اشاره نشده است و متریال wetted part مطابق با نت 1 (زیر جدول صفحه ای 5) nace می باشد.
6 | موارد مربوط به PURCHASING DATA به گزينه will be finalized تغيير پيدا كند. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | اعمال شد.
7 | آيتم مربوط به Element Type بايد مطابق با spec در نظر گرفته شود. |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | در بند 11 مدرک Specification For Instrumentation ، به نوع element دیافراگم سیل اشاره شده است ولی نوع element تجهیز pressure transmitter ، همان diphragm می باشد که در این مدرک نیز به آن اشاره شده است.
Process Comments
8 | Design pressure shall be revised according to PEDCO & NISOC comments on related P&ID document (T-0503) |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | process data such as design preocess has been reviewed according to the last cordination with process group.
9 | Operating pressure shall be revised according to PEDCO & NISOC comments on related PFD document (T-0508) |  | BK-SUR-ENG-INS-00-03250 | 2022-02-27 | process data such as operating preocess has been reviewed according to the last cordination with process group.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: S.Akbari | Signature |  |  |  | Clarified By: | Signature
| Date: 26 Feb 2022 |  |  |  |  | Date: