| Local Control Station (LCS) for GCS Motors |  |  |
| --- | --- | --- |
| General Requirement |  |  |
| - Selector Switch: 3Position, Local/of/Remote or (Hand/off/Auto), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Contact) - Stop Push Button: Red Color & Stay Put (Mushroom type), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Contact) - Start Push Button: Green Color & Spring Return Type, Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Contact) - Cast Iron or Copper Free Aluminum - Terminal: 10 Numbers 2.5mm2 with Spare Terminal - Suitable Earth Lug/Terminal for Internal and External With 25 mm2 - Tag Identification: Stainless Steel & Attached with Mechanical Non-Corrosive Hardware. - Control Voltage: 230 VAC - Breaking Current: 10 A - Number of Gland: 2 No. |  |  |
| 1- Explosion Proof LV LCS Type B1 (Without Ammeter) |  |  |
| ITEM | Description | Ammeter |
|  | - Cable Gland: M32 Size, EX"d", ZONE 2,IIB, T3, Nickle Plated Brass, one of entries shall be equipped with Exd Stopper Plug. - Cable: 7×2.5 mm2 | - |
|  | P-2203A | - |
|  | P-2203B | - |
|  | P-2202A | - |
|  | P-2202B | - |
|  | P-2201A | - |
|  | P-2201B | - |
|  | P-2103A | - |
|  | P-2103B | - |
| 2- Explosion Proof LV LCS Type B2 (With Ammeter) |  |  |
|  | - Cable Gland: M32 Size, EX"d", ZONE 2,IIB, T3, Nickle Plated Brass, one of entries shall be equipped with Exd Stopper Plug. - Required (Suitable for Connecting to CT X:1A ), CL 1.5. - Cable: 10×2.5 mm2 | - |
|  | AC-2121A (18.5 Kw) | 0~65A - 6×In |
|  | AC-2122A (18.5 Kw) | 0~65A - 6×In |
|  | AC-2121B (18.5 Kw) | 0~65A - 6×In |
|  | AC-2122B (18.5 Kw) | 0~65A - 6×In |
|  | AC-2121C (18.5 Kw) | 0~65A - 6×In |
|  | AC-2122C (18.5 Kw) | 0~65A - 6×In |
|  | AC-2131A (18.5 Kw) | 0~65A - 6×In |
|  | AC-2132A (18.5 Kw) | 0~65A - 6×In |
|  | AC-2131B (18.5 Kw) | 0~65A - 6×In |
|  | AC-2132B (18.5 Kw) | 0~65A - 6×In |
|  | AC-2131C (18.5 Kw) | 0~65A - 6×In |
|  | AC-2132C (18.5 Kw) | 0~65A - 6×In |
|  | P-2101A (30 Kw) | 0~75A - 6×In |
|  | P-2101B (30 Kw) | 0~75A - 6×In |
| 3- Safe Area LV LCS Type B1 (Without Ammeter) |  |  |
|  | - Cable Gland: M32 Size, Industrial Type, Nickle Plated Brass, one of enteries shall be equipped with Exd Stopper Plug. - Cable: 7×2.5 mm2. | - |
|  | P-2209 | - |
|  | P-2206 | - |
|  | P-2104 | - |

Type B1: Includes start and stop pushbuttons plus a three position selector switch.

Type B2: Includes start and stop pushbuttons plus a three position selector switch and an ammeter.