| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| CAMP HAVC ATTACHMENT نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Class: |  | CLIENT Doc. Number: |  |  |  |  |
| Status: | IDC: Inter-Discipline Check IFC: Issued For Comment IFA: Issued For Approval AFD: Approved For Design AFC: Approved For Construction AFP: Approved For Purchase AFQ: Approved For Quotation IFI: Issued For Information AB-R: As-Built for CLIENT Review AB-A: As-Built –Approved |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | D00 | D01 | D02 | D03 | D04 |  | PAGE | D00 | D01 | D02 | D03 | D04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  | 51 |  |  |  |  |  |
| 2 |  |  |  |  |  |  | 52 |  |  |  |  |  |
| 3 |  |  |  |  |  |  | 53 |  |  |  |  |  |
| 4 |  |  |  |  |  |  | 54 |  |  |  |  |  |
| 5 |  |  |  |  |  |  | 55 |  |  |  |  |  |
| 6 |  |  |  |  |  |  | 56 |  |  |  |  |  |
| 7 |  |  |  |  |  |  | 57 |  |  |  |  |  |
| 8 |  |  |  |  |  |  | 58 |  |  |  |  |  |
| 9 |  |  |  |  |  |  | 59 |  |  |  |  |  |
| 10 |  |  |  |  |  |  | 60 |  |  |  |  |  |
| 11 |  |  |  |  |  |  | 61 |  |  |  |  |  |
| 12 |  |  |  |  |  |  | 62 |  |  |  |  |  |
| 13 |  |  |  |  |  |  | 63 |  |  |  |  |  |
| 14 |  |  |  |  |  |  | 64 |  |  |  |  |  |
| 15 |  |  |  |  |  |  | 65 |  |  |  |  |  |
| 16 |  |  |  |  |  |  | 66 |  |  |  |  |  |
| 17 |  |  |  |  |  |  | 67 |  |  |  |  |  |
| 18 |  |  |  |  |  |  | 68 |  |  |  |  |  |
| 19 |  |  |  |  |  |  | 69 |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 70 |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 71 |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 72 |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 73 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 74 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 75 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 76 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 77 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 78 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 79 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 80 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 81 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 82 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 83 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 84 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 85 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 86 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 87 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 88 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 100 |  |  |  |  |  |

فهرست مطالب

1-	محاسبه بار مورد نیاز سیستم هواساز	4

2-	ساختمان NISOC Residential Building	4

3-	ساختمان NISOC Office Building	4

4-	ساختمان رانندگان (Drivers)	5

5-	ساختمان Petro Iran Residential	5

6-	ساختمان Petro Iran Office	5

7-	ساختمان Canteen	6

- محاسبه بار مورد نیاز سیستم هواساز

بر اساس مطالعات انجام شده در بینک، آمپر مصرفی کولرهای گازی موتور سنگین t3 تقریبا دو برابر کولرهای گازی اینورتردار است. از این رو:

| Electrical Power Demand (W) | Voltage (V) | Maximum Electrical Current | HVAC | Item |
| --- | --- | --- | --- | --- |
| =10×220=2200~2500 | 1 Phase/ 220 | 10 A | 12000 BTU | 1 |
| =15×220=3300~4000 | 1 Phase/ 220 | 15 A | 18000 BTU | 2 |
| =20×220=4400~5000 | 1 Phase/ 220 | 20 A | 24000 BTU | 3 |
| =25×220=5500~6000 | 1 Phase/ 220 | 25 A | 30000 BTU | 4 |

در محاسبه بار Split های هر ساختمان با توجه به تعداد دستگاهها، توانهای جدول بالا مدنظر قرار گرفته است.

- ساختمان NISOC Residential Building

بر اساس مدرک HVAC System Layout (BK-GNRAL-PEDCO-220-HV-PY-0002) تعداد Split ها و آبگرمکن های این ساختمان به قرار زیر است:

| NISOC Residential HVAC |  |  |  |  |
| --- | --- | --- | --- | --- |
| Power Demand | Number | Equipment |  | Item |
| =19×4000=76000 | 19 | 18000 Split | DX-Split Air Conditioner | 1 |
| =2×5000=10000 | 2 | 24000 Split |  | 2 |
| =2×6000=12000 | 2 | 30000 Split |  | 3 |
| =3*3000=9000 | 3 | 3 KW | Water Heater | 4 |
| 107 Kw | HVAC Total Power Demand |  |  |  |

- ساختمان NISOC Office Building

| NISOC Office HVAC |  |  |  |  |
| --- | --- | --- | --- | --- |
| Power Demand | Number | Equipment |  | Item |
| =19×4000=76000 | 19 | 18000 Split | DX-Split Air Conditioner | 1 |
| =5×6000=30000 | 5 | 30000 Split |  | 3 |
| =1*5000=5000 | 1 | 5 KW | Water Heater | 4 |
| 111 Kw | HVAC Total Power Demand |  |  |  |

- ساختمان رانندگان (Drivers)

| Driver HVAC |  |  |  |  |
| --- | --- | --- | --- | --- |
| Power Demand | Number | Equipment |  | Item |
| =1×4000=4000 | 1 | 18000 Split | DX-Split Air Conditioner | 1 |
| =1×8000=8000 | 1 | 36000 Split |  | 3 |
| =1*3000=3000 | 1 | 3 KW | Water Heater | 4 |
| 15 Kw | HVAC Total Power Demand |  |  |  |

- ساختمان Petro Iran Residential

| Petro Iran Residential HVAC |  |  |  |  |
| --- | --- | --- | --- | --- |
| Power Demand | Number | Equipment |  | Item |
| =11×4000=44000 | 11 | 18000 Split | DX-Split Air Conditioner | 1 |
| =2×5000=10000 | 2 | 24000 Split |  | 2 |
| =2×6000=12000 | 2 | 30000 Split |  | 3 |
| =1*3000=3000 | 1 | 3 KW | Water Heater | 4 |
| 69 Kw | HVAC Total Power Demand |  |  |  |

- ساختمان Petro Iran Office

| Petro Iran Office HVAC |  |  |  |  |
| --- | --- | --- | --- | --- |
| Power Demand | Number | Equipment |  | Item |
| =9×4000=36000 | 9 | 18000 Split | DX-Split Air Conditioner | 1 |
| =7×5000=35000 | 7 | 24000 Split |  | 2 |
| =1*3000=3000 | 1 | 3 KW | Water Heater | 4 |
| 72 Kw | HVAC Total Power Demand |  |  |  |

- ساختمان Canteen

| Canteen HVAC |  |  |  |  |
| --- | --- | --- | --- | --- |
| Power Demand | Number | Equipment |  | Item |
| =4×4000=16000 | 4 | 18000 Split | DX-Split Air Conditioner | 1 |
| =1×5000=5000 | 1 | 24000 Split |  | 2 |
| =6×6000=36000 | 6 | 30000 Split |  | 3 |
| =2*3000=6000 | 2 | 3 KW | Water Heater | 4 |
| 63 Kw | HVAC Total Power Demand |  |  |  |