## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض و ابنیه تحت الارض عمومی و مشترک
ELECTRICAL LOAD LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 4
9184 – 073 - 053 |  |  | BK |  | GNRAL | PEDCO | 220 |  | EL | LI | 0001 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
ELECTRICAL LOAD LIST نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | Jul.2022 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | May.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-707104
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض و ابنیه تحت‌الارض عمومی و مشترک
ELECTRICAL LOAD LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 4
9184 – 073 - 053 |  |  | BK | GNRAL |  | PEDCO | 220 | EL | LI | 0001 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 51
2 | X | X | [6 empty] | 52
3 | X | X | [6 empty] | 53
4 | X | X | [6 empty] | 54
5 | [8 empty] | 55
6 | [8 empty] | 56
7 | [8 empty] | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## Abb
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض و ابنیه تحت‌الارض عمومی و مشترک
ELECTRICAL LOAD LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 4
9184 – 073 - 053 |  |  | BK | GNRAL |  | PEDCO | 220 | EL | LI | 0001 | D01
Service Type:
N : Normal Load
E : Emergency Load
Load Duty:
C : Continuous Load
I : Intermitant Load
S : Stand By Load
LR/FL: Loacked Rotor / Full Load Current
Load Type:
M: Motor
F: Non-Motor
Definition of API Factor
1.25 for Motor Power < 22kW,
1.15 for Motor Power between, 22kW and 55kW
1.1 for Motor Power > 55kW
Height derating factor can be determined as follows if no manufacturer data is available:
|  | Height Above Sea Level |  |  | Height Factor
|  | < 1000 m |  |  | 1
|  | 1000 < Height < 1500 m |  |  | 0.97
|  | 1500 m > |  |  | 0.94
Coolant (Cooling) Factor is 0.88 according to basic document for motor feeder type.
LV Feeder Type:
F1: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for I<63A Feeders
F2: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for 63A=<I<100A Feeders
F3: Simple 4-Pole MCCB Feeder with Thermal/Magnetic Trips, for 100A=<I Feeders
F4: Simple 3-Pole MCCB Feeder with Thermal/Magnetic Trips, for I<63A Feeders
F5: Simple 3-Pole MCCB Feeder with Thermal/Magnetic Trips, for 63A=<I<100A Feeders
F6: Simple 3-Pole MCCB Feeder with Thermal/Magnetic Trips, for 100A=<I Feeders
F7: Simple 2-Pole MCCB Feeder for Feeding Single Phase Loads (Ph+N or 2-Ph)
M1: Direct on Line Motor Starter Feeders for 0.4 ≤ P < 4kW (Switch Fuse + Contactor + Bimetal + R/L Signaling)
M2: Direct on Line Motor Starter Feeders for 4kW ≤ P < 18.5kW (Switch Fuse + Contactor + Bimetal + R/L Signaling + R/L Ammeter)
M3: Direct on Line Motor Starter Feeders for 18.5kW ≤ P <30 (Switch Fuse + Contactor + Bimetal + R/L Signaling + R/L Ammeter (49, 50G, Phase Control))
M4: Direct on Line Motor Starter Feeders for 30kW ≤ P (Switch Fuse + Contactor + Overload CT + R/L Signaling + R/L Ammeter (49, 50G, Phase Control))
MV Feeder Type:
C1: 11 KV Incoming Feeder
C2: Outgoing Transformer 2000 KVA
C3: Outgoing Motor Starter <1000 KW
C4: Bus Coupler 11 KV

## Camp
Item NO | Rev | Bus | Equipment Number | Load Description | Service Type | No Phases | Rated Voltage (V) | Load Type | Rated Power (Kw) | Eff. (%) |  | Power Factor | Current Normal Operation (A)
1 | D01 | A | NISOC Office Building Panel | NO-DP | N | 3 | 400 | F | 118.76 | 100 |  | 0.9 | 190.4614
2 | D01 | A | NISOC Residental Building Panel | NR-DP | N | 3 | 400 | F | 115.28 | 100 |  | 0.9 | 184.8804
3 | D01 | A | Petro Office Building Panel | PO-DP | N | 3 | 400 | F | 80.28 | 100 |  | 0.9 | 128.7491
4 | D01 | A | Petro Residental Building Panel | PR-DP | N | 3 | 400 | F | 77.28 | 100 |  | 0.9 | 123.9379
5 | D01 | A | Restaurant Building Panel | RES-DP | N | 3 | 400 | F | 71.28 | 100 |  | 0.9 | 114.3154
6 | D00 | A | Driver Building Panel | DR-DV | N | 3 | 400 | F | 23.28 | 100 |  | 0.9 | 37.3353
7 | D00 | A | Warehouse Panel | WH-DP | N | 3 | 400 | F | 7 | 100 |  | 0.9 | 11.2263
8 | D01 | A | Workshop Panel | WSH-DP | N | 3 | 400 | F | 38.75 | 100 |  | 0.9 | 62.1453
9 | D00 | A | Gatehouse Panel | GH-DP | N | 3 | 400 | F | 5 | 100 |  | 0.9 | 8.0188
10 | D01 | A | Outdoor Area Panel | CMP-DP | N | 3 | 400 | F | 4.25 | 100 |  | 0.9 | 6.8159
Building Numbering Procedure |  |  |  | To calculate power demand, below assumptions have been considered: - Since staffs will present in one building at the same time, therefore the power consumption of NO-DP or NR-DP (each one is bigger), will be considered. This note is valid for PO-DP & PR-DP. - The power demand of other panels will be considered completely. - At the end, diversity factor “0.5” will be considered for active power. | [6 empty] | Active Power (Kw)
NO: NISOC Office | [10 empty] | 345.12
NR: NISOC Residental | [10 empty] | Active Demand (Kw)
PO: PETRO Office | [10 empty] | 172.56
PR: PETRO Residental | [10 empty] | Reactive Demand (kvar)
RES: Restaurant | [10 empty] | 75.2172
DVR: Driver
WH: WareHouse | [10 empty] | Apparent Power (Kva)
WS: WorkShop | [10 empty] | 188.2407
GH: Gate House
CMP: Camp |  |  |  | According to above calculation, one transformer 250 KVA is sufficient to supply power demand in camp area
تسهیلات
ELECTRICAL LOAD LIST
شماره صفحه: 4 از 4
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض و ابنیه تحت‌الارض
عمومی و مشترک
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
220
EL
LI
0001
D01
بسته کاری
GNRAL
پروژه
BK