## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GNRAL-PEDCO-220-EL-LI-0001_D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0970 |  |  | Transmital Date: 18-May-2022
Document Title: Electrical Load List |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0970 |  |  | Transmital Date: 18-May-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GNRAL-PEDCO-220-EL-LI-0001_D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | The reference of mentioned power in load list (Rated Power (Kw) column) shall be specified. |  | BK-SUR-ENG-ELE-01-04485 | 2022-05-30 | مطابق با مذاکرات انجام شده، در فایل ورد پیوست نحوه محاسبات بارهای سیستم هواساز مشخص شده است. بارهای روشنایی و میزان مصرف برق هر ساختمان در فایل اکسل پیوست و همچنین مدرک لیست بار درج شده است.
2 | with considering the nature of loads which are generally HVAC, lighting and small power and office loads, It seems, the value of diversity factor for demand active power (0.5) is very low. It shall be rechecked and modified base on engineering practices. |  | BK-SUR-ENG-ELE-01-04485 | 2022-05-30 | مطابق با مذاکرات انجام شده ضریب همزمانی 0.5 در نظر گرفته شده است.
3 | A percentage of NO-DP and PR-DP power consumption (for instance 20%) to be considered in the demand calculation |  | BK-SUR-ENG-ELE-01-04485 | 2022-05-30 | با توجه به اینکه ظرفیت بارهای سیستم هواساز دست بالا می باشد، لذا نیازی به در نظر گرفتن بار ذخیره نمی باشد.
4 | there is no spare capacity for future expansion in transformer sizing, please clarify. |  | BK-SUR-ENG-ELE-01-04485 | 2022-05-30 | مطابق با مذاکرات انجام شده و جلسات برقرار شده با کارفرمای محترم، دیماند مورد نیاز به 200 کیلووات می رسد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 29-May-22 |  |  |  |  | Date: