## Table 1
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک فعالیتهای رو زمینی در بستههای کاری تحتالارض ساخت موقعیت چاه، تأسیسات سرچاهی، خطوط جرياني و مربوط به موقعیت W028
TBE/TBA For WHCP/HPU
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  | BK | W028 | PEDCO | 110 | IN |  | TB | 0001 | D02
ITEM | DESCRIPTION | REQUIREMENT |  | VENDORS EVALUATION
|  |  |  | Arman Farayand Control Co |  | EPC Contractor Conclusion | Kondor Sanat Partian Industrial Group |  | EPC Contractor Conclusion | Proserv Iran(Kish) LLC | EPC Contractor Conclusion | Kardanan Shargh Co. | EPC Contractor Conclusion
GENERAL
1 | QUOTATION REFERENCE/DATE | VTA |  | Not specified. |  | - | KPS-BI-TO-TB-02-D2 Technical Proposal Wellhead Hydraulic Control Panel (Gas Drive 5000 psi, Well No.W018S) |  | - | 2112-1278 | Proposal shall be prepared individually as per well | M-PS-400211-04-100-01 (07) for W028 (Technical Proposal) | Accepted
2 | VENDOR AND ALL SUB-VENDORS SHALL BE IN THE AVL | In compliance with AVL |  | Confirmed in TCL form. But it is not implemented in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed in TCL form. But it is not implemented in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed | Accepted. | Confirmed | Accepted
3 | SUPPLY OF COMMISSIONING AND START UP SPARES | Required Spare parts for commissioning and start-up; a qualified and complete list based on "PROJECT SPARE PART SUPPLY PROCEDURE" (Doc. No. E&D-QC-SP-1). |  | Confirmed. |  | Accepted. | Confirmed. |  | Accepted. | Not confirmed. Vendor replied: Proserv Iran will provide the complete WHCP ready for site installation and hence commissioning spares are not required. | Not Accepted. This item shall be submitted by vendor. Installation is scope out. | Confirmed. | Accepted.
4 | SUPPLY OF 2 YEARS OPERATING SPARES | Spare parts for two years operation; a qualified and complete list based on "PROJECT SPARE PART SUPPLY PROCEDURE" (Doc. No. E&D-QC-SP-1) |  | Confirmed. |  | Accepted. | Confirmed. |  | Accepted. | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Confirmed | Accepted
5 | SUPPLY OF SPECIAL TOOLS WITH ITEMIZED PRICE LIST | Vendor shall propose the list of special tools needed for installation, operation and maintenance of this panel during the bid. The list shall be Accepted by the company. |  | Confirmed in TCL form. But it is not implemented in technical offer (such as one common portable hydraulic hand pump for opening SSV/SSSV). |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed. |  | Accepted. | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Confirmed | Accepted
6 | GUARANTEE TERMS | The guarantee period shall be eighteen (18) months from the date of delivery or twelve (12) months from the installation date of each equipment/packages at site. Vendor shall be able to provide spares back up and support for the plant life of at least 20 years. |  | Guarantee period confirmed in TCL form but support for the plant life of at least 20 years is not confirmed. |  | Accepted.( Guarantee term is accepted but vendor to consider support for the plant life of at least 20 years to the proposal.) | Guarantee period confirmed in TCL form but support for the plant life of at least 20 years is not confirmed. |  | Accepted.( Guarantee term is accepted but vendor to consider support for the plant life of at least 20 years to the proposal.) | Guarantee period confirmed in TCL form but support for the plant life of at least 20 years is not confirmed. | Accepted.( Guarantee term is accepted but vendor to consider support for the plant life of at least 20 years to the proposal.) | Confirmed | Accepted
7 | TECHNICAL EXCEPTION/DEVIATION LIST | Required |  | Included. |  | Major deviation. Not Accepted. | Included. |  | Accepted due to Client approval | Included. | Major deviation. Not Accepted. | Included. | Accepted
8 | EQUIPMENT CATALOUGE | Required |  | Included. |  | Accepted. | Included. |  | Accepted. | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Included. | Accepted.
9 | INSPECTION AND TEST PLAN | According to the project document |  | Included |  | Accepted due to Client Approval | Included |  | Accepted due to Client Approval | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Included | Accepted ( will be finalized as per client points of view)
10 | FAT AND SAT PROCEDURE | Required |  | Included. |  | Accepted due to Client Approval | Included |  | Accepted due to Client Approval | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Only FAT is included. SAT as per contract. | Accepted
11 | PROVEN DESIGN MANUFACTURING AND EXPERIENCE | Required |  | Confirmed in TCL form replied by vendor. But it is not included in technical offer |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed in TCL form replied by vendor. But it is not included in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Included. | Accepted. | Included | Accepted.
12 | PROCEDURE FOR SURFACE PREPARATION AND PAINTING | Required |  | Vendor replied painting is not applicable. |  | Accepted. | Vendor replied painting is not applicable. |  | Accepted. | Vendor replied painting is not applicable. | Accepted. | painting is not applicable. | Accepted.
13 | LETTER OF CONFORMITY | Required |  | Not included |  | Not Accepted. To be added to the vendor proposal. | Confirmed in TCL form. But it is not implemented in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | As per vendor instruction | Accepted.
14 | WHCP DESIGN RATING | 5000 psi |  | Confirmed. |  | Accepted. | Confirmed. |  | Accepted. | Confirmed. | Accepted. | Confirmed. | Accepted.
15 | HYDRAULIC POWER UNIT GENERAL REQUIREMENTS (PRELIMINARY, FINAL DATA SHALL BE SUBMITTED BY PURCHASER AFTER PO.) | Vendor to supply hydraulic power unit as below: - SSSV actuator swept volume: 2.5 lit. - SSV actuator swept volume: 5 lit. - SSSV/ SSV opening time: 8 sec. - SSSV / SSV closure time: 2 sec. - SSSV Crack open hydraulic pressure : 3000 PSI - SSV Crack open hydraulic pressure: 2500 Psi - SSSV Actuator hydraulic Design pressure : 5000 PSI - SSV Actuator hydraulic Design pressure : 3000 PSI - SSSV Maximum Working Pressure: 5000 PSI - SSV Maximum Working Pressure: 3000 PSI - SSSV Hydraulic Tube Connection: ¼ “ (2 No.s for supply and return line) - SSV Hydraulic Tube Connection: ½ “ |  | Not Confirmed |  | Not Accepted. | Accepted ( Deviation for action time as per vendor deviation list). |  | Accepted ( Deviation will be close in case of Client approval.) | Accepted ( Deviation as per vendor deviation list). | Accepted ( Deviation will be close in case of Client approval.) | Accepted ( Deviation for action time as per vendor deviation list). | Accepted ( Deviation will be close in case of Client approval.)
16 | HYDRAULIC POWER UNIT (SSV&SSSV ACTUATION PRESSURE) | Vendor to confirm: -High hydraulic header pressure for actuation of SSSV (5000PSI) -Medium hydraulic header pressure for actuation of SSV (3000PSI) |  | Not Confirmed |  | Not Accepted. | Confirmed in TCL form. But it is shall be implemented in updated technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed | Accepted. | Confirmed | Accepted
17 | CABINET INGRESS PROTECTION | The cabinet shall be fully enclosed providing equipment protection IP65 as a minimum side doors shall be used for maintenance. An IP65 test certificate shall be supplied. |  | Not Confirmed |  | Not Accepted. | Confirmed |  | Accepted. | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Confirmed | Accepted.
18 | CABINET THICKNESS AND MATERIAL | The cabinet shall be 3 mm minimum thickness sheet AISI 316 stainless steel |  | Not Confirmed.(Vendor replied to supply Box & Doors in 2mm wall thickness in 316ss .) |  | Not Accepted. | Vendor proposed SS 304 which is more practical and suitable. |  | Approved. (Technically acceptance will be closed in case of Client approval). | Confirmed | Accepted. | Vendor proposed SS 304 which is more practical and suitable. | Approved. (Technically acceptance will be closed in case of Client approval).
19 | PUMPS | 1- For manual applications, hand pump shall be used. This pump will be installed inside the panel to pressurize the hydraulic system to the highest pressure level in the panel. 2-To keep the pressure of hydraulic line in normal operation, a N2 driven pump is needed to generate the highest pressure level in the panel. |  | Confirmed in TCL form. But N2 driven pump is not implemented in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed. |  | Accepted. | Confirmed | Accepted. | Confirmed | Accepted.
20 | HYDRAULIC OIL RESERVOIR | Shall be equipped minimally with filter / breather, level gauge and drain valve |  | Not confirmed. |  | Not Accepted. | Confirmed. |  | Accepted. | Confirmed. | Accepted. | Confirmed. | Accepted.
21 | ESD/ RESET PUSH BUTTON FOR EACH WELL | Required as per document "Specification For WHCP/HPU". |  | Confirmed in TCL form. But it is not implemented in technical offer. |  | Not Accepted. Vendor to implement this item in general arrangement drawing of panel in technical offer. | Not Included |  | Not Accepted. | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated.( Vendor to implement this item in general arrangement drawing of panel in technical offer.) | Confirmed | Accepted
22 | STATUS INDICATORS ,PRESSURE GAUGES AND PUSH BUTTONS IN PANEL FRONT FACE | Required |  | Not Confirmed |  | Not Accepted. | Confirmed in TCL form. But it is not implemented in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. (Some items shall be added to the front face of panel like ESD reset pushbutton by vendor.) | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Confirmed | Accepted
23 | QUICK EXHAUST VALVE OPTION FOR SSV/SSSV(VTC) | Required |  | Not Confirmed |  | Not Accepted. | Vendor confirm to supply QEV for SSV. |  | Accepted. | Confirmed. | Accepted. | Vendor confirm to supply QEV for SSV. QEV for SSSV is not applicable | Accepted.
24 | TUBE AND FITTING FOR SSV/SSSV/FUSIBLE PLUG | All required tube and fitting for SSSV / SSV/ fusible plug Shall be supplied as per documents "Instrument Hook up Drawing" and "MTO for instrument tube & fittings" |  | Not Confirmed |  | Not Accepted. | Confirmed. (Just tube size of 2SV is deviated by vendor). |  | Accepted. Just vendor to consider the convertor connection 3/8" to 1/2 for SSV(Deviation accepted by Hirganenergy co.and will be closed due to Client approval.) | Confirmed | Accepted. Tube length shall be updated refer to the latest documents" MTO for Instrument Tube & Fittings". Also return line/pipe to the SSV/SSSV shall be considered by vendor. | Confirmed. | Accepted.
25 | CORRECT AND SAFE OPERATION OF THE UNIT, PROVIDING ALL SAFETY PROTECTION DEVICES. | Required |  | Confirmed |  | Accepted. | Confirmed |  | Accepted. | Confirmed | Accepted. | Confirmed. | Accepted.
26 | ONE ADJUSTABLE DELAY: OPEN SEQUENCE SSV: SSV CAN BE OPENED AFTER AN ADJUSTABLE TIME DELAY AFTER SSSV OPENING CLOSE SEQUENCE SSSV: SSSV SHALL BE CLOSED AFTER AN ADJUSTABLE TIME DELAY AFTER SSV CLOSING. | Required as per document "RR-00-PS-110-IN-SP-0014,Specification For WHCP/HPU"./VTA |  | Confirmed for closing but not Confirmed for opening. |  | Accepted. Vendor to implement opening time delay for SSV/SSSV in technical proposal | Confirmed in TCL form. But it is not implemented in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Confirmed | Accepted
27 | FILTER | Shall be considered filter at entry of the tank and at suction line of the pumps( with indicator) |  | Not Confirmed. |  | Not Accepted. | Confirmed in TCL form. But it is not implemented in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Confirmed | Accepted
28 | NUMBER OF OIL TANK \ VOLUME FOR OIL TANK | 2 (two hydraulic oil Tank is required : one for hydraulic reservoir and A separate oil tank should be supplied for SSSV return line as spec. ) \ VTA |  | Not Confirmed. Only 1 tank has been considered. |  | Not Accepted. | Confirmed. |  | Accepted. | Confirmed. | Accepted. | Confirmed | Accepted.
29 | WHCP EXTERNAL CONNECTION | - Oil line to SSV:½” - Oil line to SSSV: ¼” - Drain line for panel cleaning : ½” - Crude oil line to PSHH, PSLL,(before and after choke flange): ½” - Nitrogen Line To Fusible Plugs (3No for each panel): ¼” -External hand pump connection: 1/2" (VTA) |  | Confirmed in TCL form. But it is not implemented in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed. (Just vendor deviated the connection size of SSV to 3/8") |  | Accepted ( Deviation accepted by Hirganenergy co.and will be closed due to Client approval.) | Not confirmed in P&ID of panel in technical proposal of vendor. | Not Accepted. | Confirmed | Accepted.
30 | NUMBER OF FUSIBLE PLUG FOR EACH WELL | 3 |  | Confirmed in TCL form. But it is not implemented in technical offer |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed |  | Accepted. | Confirmed in TCL form. But it is not implemented in technical offer. | accepted as per TCL. Technical proposal to be updated. | Confirmed | Accepted.
31 | ACCUMULATORS | Shall be sized and supplied by Vendor |  | Not Confirmed and deviated by vendor. |  | Not Accepted. | Deviated by vendor. (Vendor replied: One accumulator in header line is enough.) |  | Accepted ( Deviation accepted by Hirganenergy co.and will be closed due to Client approval.) | Deviated by vendor. (Vendor replied: One accumulator in header line is enough.) | Accepted ( Deviation accepted by Hirganenergy co.and will be closed due to Client approval.) | One accumulator in header line (sufficient volume) is considered | Accepted (Technical acceptance will be closed due to Client approval.)
32 | MANIFOLD FOR GAUGES | Min SS 316L, 2 valve block manifold shall be provided. |  | Included.(in the installation kit list) |  | Accepted. | Not confirmed. Vendor replied: Needle valves for block and bleed will be considered by vendor. |  | Accepted ( Deviation accepted by Hirganenergy co.and will be closed due to Client approval.) | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Needle valves for block and bleed will be considered by vendor. | Accepted (Technical acceptance will be closed due to Client approval.)
33 | FIRST OUT INDICATOR SHALL BE CONSIDERED FOR WHCP | The panel shall be supplied with “FIRST OUT” feature so the panel logic shall be designed in a manner that first cause of panel shutdown be distinguishable for maintenance purposes. |  | Included. |  | Accepted just location of first out indicator is not cleared in P&ID and vendor to specify it. | Included in vendor confirmation letter But it is not implemented in technical offer. |  | Accepted as per vendor confirmation letter. Technical proposal to be updated. | Confirmed. | Accepted. | Confirmed. | Accepted
34 | ALL PRESSUERIZED TBES SHALL BE PROTWCTED WITH A TEMPARATURE RELIEF VALVE (TRV) | to be protected against high pressure because of trapped oil expansion. |  | Not Confirmed and deviated by vendor. |  | Not Accepted. | Confirmed |  | Accepted. | Confirmed. | Accepted. | N/A Since all the section of WHCP is protected from overpressure by means of relief valves, there is no need to consider TRV for these sections | Approved. (Technically acceptance will be closed in case of Client approval).
35 | NAME PLATE | a name plate with the project name and No. of WHCP Required. |  | Confirmed in TCL form. But it is not implemented in technical offer |  | Accepted. | Confirmed in TCL form. But it is not implemented in technical offer |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed in TCL form. But it is not implemented in technical offer. | Accepted as per TCL. Technical proposal to be updated. | Confirmed. | Accepted.
36 | OVERRIDE SYSTEM FOR START-UP | AN OVERRIDE SYSTEM FOR START-UP IN CASE OF LACK OF PRESSURE TO BYPASS LOW PRESSURE SWITCH IN FLOW LINE FOR LIMITED TIME SHALL BE CONSIDERED. |  | Not specified. |  |  | Confirmed |  | Accepted. | Confirmed | Accepted. | Confirmed | Accepted.
37 | VENDOR TO CONFIRM FOR PANEL LOGICS AND FUSIBLE PLUG THE NITROGEN PRESSURE IS CONSIDERED. |  |  | Not Confirmed and deviated by vendor. |  | Not Accepted. | Confirmed |  | Accepted. | Confirmed | Accepted. | Confirmed | Accepted.
38 | VENDOR TO SUPPLY AUTOMATIC DRAIN VALVE FOR NITROGEN SUPPLY LINE. |  |  | Not Confirmed and deviated by vendor. |  | Not Accepted. | Confirmed |  | Accepted. | Not confirmed. | Not Accepted. | Confirmed | Accepted.
NITROGEN BOTTLES
39 | NUMBER OF BOTTLES | The WHCP Vendor is responsible for design of suitable pressure and volume of Nitrogen for SSV and SSSV on\off operation. For calculation of bottle sizes below notes to be considered, • At least two times actuation of each valve are required • At least six months operation of WHCP without refill is needed at worst scenario (for each of Nitrogen banks). Above calculation shall be submitted by Vendor. |  | Not confirmed. |  | Not Accepted. | Confirmed in TCL form. But it is not implemented in technical offer. |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed. | Accepted. | Confirmed. | Accepted.
40 | SIZE AND PRESSURE OF BOTTLES | As a minimum: two racks with 4 bottles with capacity of 50 liter |  | Not confirmed. |  | Not Accepted. | Confirmed in TCL form. But it is not implemented in technical offer |  | Accepted as per TCL. Technical proposal to be updated. | Confirmed. | Accepted. | Confirmed | Accepted.
41 | NITROGEN AND OIL CHARGING KIT | Required |  | Not confirmed. |  | Not Accepted. | Confirmed. |  | Accepted. | Confirmed. | Accepted. | Confirmed | Accepted.
42 | A PRESSURE GAUGE AND A LOW PRESSURE SWITCH FOR EACH NITROGEN HEADER BOTTLE | Required |  | Not confirmed. |  | Not Accepted. | Confirmed |  | Accepted. | Not confirmed. | Not Accepted. | Pressure indicator will be provided but Low pressure Switch is not required since there is no logic for that). | Accepted. (Technical acceptance will be closed in case of Client approval.
43 | NECESSARY REQUIREMENTS FOR CHANGEOVER BETWEEN SETS OF NITROGEN BOTTLES SO RESERVED ONE COULD BE IN SERVICE WITHOUT ANY INTERRUPT SO LOW PRESSURE BOTTLES COULD BE RECHARGED OR REPLACED. | Required |  | Confirmed in TCL form. But it is not implemented in technical offer |  | Accepted as per TCL. Technical proposal to be updated. | Not confirmed. Vendor replied: Each nitrogen bottle has separate valve and each header has a separate valve. |  | Accepted. (Technically accepted by Hirganenergy co. but this item will be closed due to Client approval. | Confirmed. | Accepted. | Deviated by vendor.Automatic Changeover will not be provided. | Accepted. (Technical acceptance will be closed in case of Client approval.
44 | SEPARATE SSSV RETURN OIL LINE | Required |  | Not confirmed. |  | Not Accepted. | Confirmed |  | Accepted. | Not confirmed. | Not Accepted. | Confirmed | Accepted.
PILOT VALVES
45 | PILOT VALVES SHALL BE USED AS HYDRAULIC PRESSURE SWITCHES TO ACTIVATE PNEUMATIC LOGICS | Two High-High and two Low-Low Pressure switches for flow line shall be mounted in the WHCP so a pressure sensing line from flow-line shall be installed between WHCP and each sensing point (one before choke flange and one after choke flange) |  | Deviated.(Vendor replied to supply SAD pilot sensing pressure and this pilot active by pneumatic pressure.) |  | Accepted. | Confirmed |  | Accepted. | Confirmed | Accepted. | Confirmed | Accepted.
46 | PILOT VALVES (FOR SSSV/SSV) WITH SUITABLE BYPASS LINE FOR MANUAL STARTUP OPTION |  |  | Not confirmed. |  | Not Accepted. | Not included. Vendor replied :Due to safety action of high/low pilots, it is not recommended to consider by pass line for high pressure switch. For low pressure by pass pin will be considered on switch for startup stage. |  | Accepted( Deviation accepted by Hirganenergy co.and will be closed due to Client approval.) | Confirmed | Accepted. | Confirmed | Accepted.
47 | THE WETTED PARTS SHALL BE SUITABLE FOR NACE MR0175/ISO15156-1 REQUIREMENTS. | Required |  | Confirmed(Vendor replied wetted part for pressure sensing lines are in compliance with nace but without nace certificate) |  | Not Accepted. | Confirmed in TCL form. But it is not implemented in technical offer |  | Accepted. | Not confirmed. | Not Accepted. | Confirmed | Accepted.
INTERCONNECTING TUBE AND FITTINGS
48 | INTERCONNECTING TUBE AND FITTING | Required |  | Confirmed |  | Accepted. | Confirmed |  | Accepted. | Confirmed | Accepted. | Confirmed | Accepted.
VENDOR DOCUMENTATION
49 | VENDOR DOCUMENTATION REQUIRED AS PER MR | Required |  | Confirmed |  | Accepted. | Confirmed |  | Accepted. | Confirmed | Accepted. | Confirmed | Accepted.
FINAL CONCLUSION | [5 empty] | CA |  |  | A |  | A |  | A
LEGENDS
A = ACCEPTABLE (TECHNICALLY MEETS REQUIREMENT)
NA= NOT ACCEPTABLE (TECHNICALLY DOES NOT MEET REQUIREMENT)
CA= CONDITIONALLY ACCEPTED
INA = INFORMATION NOT AVAILABLE
N/A = NOT APPLICABLE
D02