## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LOCAL CONTROL STATIONS (LCS)
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 7
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | EL | DT | 0006 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR LOCAL CONTROL STATIONS (LCS) نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | Jul.2022 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | May.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | Feb.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-709023
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LOCAL CONTROL STATIONS (LCS)
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 7
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | DT | 0006 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 51
2 | X | X | X | [5 empty] | 52
3 | X | X | [6 empty] | 53
4 | X | X | [6 empty] | 54
5 | X | X | [6 empty] | 55
6 | X | X | [6 empty] | 56
7 | X | X | [6 empty] | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## B1-LV-EX
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LOCAL CONTROL STATIONS (LCS)
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 7
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | EL | DT | 0006 | D02
Explosion Proof LV LCS Type B1
A | Electrical Specification |  |  |  | Purchaser Requirement |  |  |  |  | Vendor Data
Equipment Tag Number
1. General data | 1.1 | Reference Document |  |  | BK-GNRAL-PEDCO-000-EL-SP-0008 IPS-M-EL-161(2)
| 1.2 | Type of LCS according to IPS |  |  | B1-LV-EX
| 1.3 | Type of Protection |  |  | EEX"d"
| 1.4 | Explosion Group |  |  | IIB
| 1.5 | Temperature Class |  |  | T3
| 1.6 | Zone |  |  | 2
| 1.7 | Degree of Protection |  |  | IP 65
| 1.8 | Average Ambient Temperature |  |  | Max 55 °C, Min 5 °C
| 1.9 | Elevation from Sea Level |  |  | 12.5 m
| 1.1 | Maximum Humidity |  |  | 100%
| 1.11 | Location |  |  | Binak Oilfield in Busheher Province
| 1.12 | Isolation Voltage |  |  | 1000V
2.Technical Data | 2.1 | Control Voltage |  |  | 230 Vac
| 2.2 | Breaking Current |  |  | 10 A
| 2.3 | Cable |  |  | 7×2.5 mm2
| 2.4 | Cable Gland with PVC Shroud |  |  | Required
| 2.5 | Number of Gland |  |  | 2
| 2.6 | Size of Terminal |  |  | 4 mm2 with Spare Terminal
| 2.7 | Termination |  |  | Wired to Device Terminal
| 2.8 | Material/Thichness |  |  | Cast Iron or Copper Free Aluminum
| 2.9 | Current Rating |  |  | N/A
| 2.1 | No. of Terminal |  |  | 10 No.
| 2.11 | Color Code |  |  | RAL 7032
3. Accessories | 3.1 | Stop Push Button: Red Color & Stay Put (Mushroom type), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.2 | Start Push Button: Green Color & Spring Return Type,Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.3 | Selector Switch: 3Position, Local/Of/Remote or (Hand/off/Auto), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.4 | Earth Terminal: Required, Internal & External, External is 25mm2.
| 3.5 | Cable Gland: M32 Size, EEX"d", ZONE 2,IIB, T3, Nickle Plated Brass, one of enteries shall be equipped with Exd Stopper Plug.
| 3.6 | Installation Type with all Accessories: BK-GNRAL-PEDCO-000-EL-DW-0004
| 3.7 | Tag Identification: Stainless Steel & Attached with Mechanical Non-Corrosive Hardware.
B | General Note
1 | Type of Control Cable is CU/XLPE/SWA/PVC or CU/XLPE/LC/SWA/PVC
2
3

## B2-LV-EX
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LOCAL CONTROL STATIONS (LCS)
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 7
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | EL | DT | 0006 | D02
Explosion Proof LV LCS Type B2
A | Electrical Specification |  |  |  | Purchaser Requirement |  |  |  |  | Vendor Data
Equipment Tag Number
1. General data | 1.1 | Reference Document |  |  | BK-GNRAL-PEDCO-000-EL-SP-0008 IPS-M-EL-161(2)
| 1.2 | Type of LCS according to IPS |  |  | B2-LV-EX
| 1.3 | Type of Protection |  |  | EEX"d"
| 1.4 | Explosion Group |  |  | IIB
| 1.5 | Temperature Class |  |  | T3
| 1.6 | Zone |  |  | 2
| 1.7 | Degree of Protection |  |  | IP 65
| 1.8 | Average Ambient Temperature |  |  | Max 55 °C, Min 5 °C
| 1.9 | Elevation from Sea Level |  |  | 12.5 m
| 1.1 | Maximum Humidity |  |  | 100%
| 1.11 | Location |  |  | Binak Oilfield in Busheher Province
| 1.12 | Isolation voltage |  |  | 1000 V
2.Technical Data | 2.1 | Control Voltage |  |  | 230 Vac
| 2.2 | Breaking Current |  |  | 10 A
| 2.3 | Cable |  |  | 10×2.5 mm2
| 2.4 | Cable Gland with PVC Shroud |  |  | Required
| 2.5 | Number of Gland |  |  | 2
| 2.6 | Size of Terminal |  |  | 4 mm2 with Spare Terminal
| 2.7 | Termination |  |  | Wired to Device Terminal
| 2.8 | Material/Thichness |  |  | Cast Iron or Copper Free Aluminum
| 2.9 | Ammeter |  |  | Required (suitable for connecting to CT X:1A ), CL 1.5
| 2.1 | Current Rating |  |  | According to SLDs
| 2.11 | No. of Terminal |  |  | 10 No.
| 2.12 | Color Code |  |  | RAL 7032
3. Accessories | 3.1 | Stop Push Button: Red Color & Stay Put (Mushroom type), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.2 | Start Push Button: Green Color & Spring Return Type,Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.3 | Selector Switch: 3Position, Local/Of/Remote or (Hand/off/Auto), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.4 | Earth Terminal: Required, Internal & External, External is 25mm2.
| 3.5 | Cable Gland: M32 Size, EEX"d", ZONE 2,IIB, T3, Nickle Plated Brass, one of enteries shall be equipped with Exd Stopper Plug.
| 3.6 | Installation Type with all Accessories: BK-GNRAL-PEDCO-000-EL-DW-0004
| 3.7 | Tag Identification: Stainless Steel & Attached with Mechanical Non-Corrosive Hardware.
B | General Note
1 | Type of Control Cable is CU/XLPE/SWA/PVC or CU/XLPE/LC/SWA/PVC
2 | Ammeters shall have a compressed overload scale of at least 6 times the full load motor current.
3

## B1-LV-WP
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LOCAL CONTROL STATIONS (LCS)
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 7
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | EL | DT | 0006 | D02
Safe Area LV LCS Type B1
A | Electrical Specification |  |  |  | Purchaser Requirement |  |  |  |  | Vendor Data
Equipment Tag Number
1. General data | 1.1 | Reference Document |  |  | BK-GNRAL-PEDCO-000-EL-SP-0008 IPS-M-EL-161(2)
| 1.2 | Type of LCS according to IPS |  |  | B1-LV-WP
| 1.3 | Type of Protection |  |  | Weather Proof
| 1.4 | Explosion Group |  |  | -
| 1.5 | Temperature Class |  |  | -
| 1.6 | Zone |  |  | Safe Area
| 1.7 | Degree of Protection |  |  | IP 55
| 1.8 | Average Ambient Temperature |  |  | Max 55 °C, Min 5 °C
| 1.9 | Elevation from Sea Level |  |  | 12.5 m
| 1.1 | Maximum Humidity |  |  | 100%
| 1.11 | Location |  |  | Binak Oilfield in Busheher Province
| 1.12 | Isolation voltage |  |  | 1000V
2.Technical Data | 2.1 | Control Voltage |  |  | 230 Vac
| 2.2 | Breaking Current |  |  | 10 A
| 2.3 | Cable |  |  | 7×2.5 mm2
| 2.4 | Cable Gland with PVC Shroud |  |  | Required
| 2.5 | Number of Gland |  |  | 2
| 2.6 | Size of Terminal |  |  | 4 mm2 with Spare Terminal
| 2.7 | Termination |  |  | Wired to Device Terminal
| 2.8 | Material/Thichness |  |  | Cast Iron or Copper Free Aluminum
| 2.9 | Current Rating |  |  | N.A
| 2.1 | No. of Terminal |  |  | 10 No.
| 2.11 | Color Code |  |  | RAL 7032
3. Accessories | 3.1 | Stop Push Button: Red Color & Stay Put (Mushroom type), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.2 | Start Push Button: Green Color & Spring Return Type,Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.3 | Selector Switch: 3Position, Local/Of/Remote or (Hand/off/Auto), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.4 | Earth Terminal: Required, Internal & External, External is 25mm2.
| 3.5 | Cable Gland: M32 Size, Industrial Type, Nickle Plated Brass, one of enteries shall be equipped with Exd Stopper Plug.
| 3.6 | Installation Type with all Accessories: BK-GNRAL-PEDCO-000-EL-DW-0004
| 3.7 | Tag Identification: Stainless Steel & Attached with Mechanical Non-Corrosive Hardware.
B | General Note
1 | Type of Control Cable is CU/XLPE/SWA/PVC or CU/XLPE/LC/SWA/PVC
2
3

## B2-LV-WP
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LOCAL CONTROL STATIONS (LCS)
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 7
9184 – 073 - 053 |  |  | BK | GCS | PEDCO | 120 | EL | DT | 0006 | D02
Safe Area LV LCS Type B2
A | Electrical Specification |  |  |  | Purchaser Requirement |  |  |  |  | Vendor Data
Equipment Tag Number
1. General data | 1.1 | Reference Document |  |  | BK-GNRAL-PEDCO-000-EL-SP-0008 IPS-M-EL-161(2)
| 1.2 | Type of LCS according to IPS |  |  | B2-LV-WP
| 1.3 | Type of Protection |  |  | Weather Proof
| 1.4 | Explosion Group |  |  | -
| 1.5 | Temperature Class |  |  | -
| 1.6 | Zone |  |  | Safe Area
| 1.7 | Degree of Protection |  |  | IP 55
| 1.8 | Average Ambient Temperature |  |  | Max55 °C, Min 5 °C
| 1.9 | Elevation from Sea Level |  |  | 12.5m
| 1.1 | Maximum Humidity |  |  | 100%
| 1.11 | Location |  |  | Binak Oilfield in Busheher Province
| 1.12 | Isolation voltage |  |  | 1000V
2.Technical Data | 2.1 | Control Voltage |  |  | 230 Vac
| 2.2 | Breaking Current |  |  | 10 A
| 2.3 | Cable |  |  | 10×2.5 mm2
| 2.4 | Cable Gland with PVC Shroud |  |  | Required
| 2.5 | Number of Gland |  |  | 2
| 2.6 | Size of Terminal |  |  | 4 mm2 with Spare Terminal
| 2.7 | Termination |  |  | Wired to Device Terminal
| 2.8 | Material/Thichness |  |  | Cast Iron or Copper Free Aluminum
| 2.9 | Ammeter |  |  | Required (suitable for connecting to CT X:1A ), CL 1.5
| 2.1 | Current Rating |  |  | According to SLDs
| 2.11 | No. of Terminal |  |  | 10 No.
| 2.12 | Color Code |  |  | RAL 7032
3. Accessories | 3.1 | Stop Push Button: Red Color & Stay Put (Mushroom type), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.2 | Start Push Button: Green Color & Spring Return Type,Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.3 | Selector Switch: 3Position, Local/Of/Remote or (Hand/off/Auto), Double Break Contact (1 Pair Normally Open Contact, 1 Pair Closed Open Contact)
| 3.4 | Earth Terminal: Required, Internal & External, External is 25mm2.
| 3.5 | Cable Gland: M32 Size, Industrial Type, Nickle Plated Brass, one of enteries shall be equipped with Exd Stopper Plug.
| 3.6 | Installation Type with all Accessories: BK-GNRAL-PEDCO-000-EL-DW-0004
| 3.7 | Tag Identification: Stainless Steel & Attached with Mechanical Non-Corrosive Hardware.
B | General Note
1 | Type of Control Cable is CU/XLPE/SWA/PVC or CU/XLPE/LC/SWA/PVC
2 | Ammeters shall have a compressed overload scale of at least 6 times the full load motor current.
3

## Att1
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR LOCAL CONTROL STATIONS (LCS)
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 7
9184 – 073 - 053 |  | BK | GCS | PEDCO | 120 | EL | DT | 0006 | D02
Type B1: Includes start and stop pushbuttons plus a three position selector switch.
Type B2: Includes start and stop pushbuttons plus a three position selector switch and an ammeter.