## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR NGR
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 4
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | EL | DT | 0013 | D01
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR NGR نگهداشت و افزایش تولید میدان نفتی بینک
D01 |  | Jul.2022 |  | AFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | Apr.2022 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-709030
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEETS FOR NGR
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 4
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | DT | 0013 |  | D01
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | [6 empty] | 51
2 | X | X | [6 empty] | 52
3 | X | X | [6 empty] | 53
4 | X | X | [6 empty] | 54
5 | [8 empty] | 55
6 | [8 empty] | 56
7 | [8 empty] | 57
8 | [8 empty] | 58
9 | [8 empty] | 59
10 | [8 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## NGR
Technical Data For NGR
Rev | Item | Description | Required | Vendor Data
1.Environmental Data
D00 | 1.1 | Name of Project / Plant | Binak Oilfield in Bushehr Province
D01 | 1.2 | Average Ambient Temperature (Min/Max) | Min ~ Max: +5 ~ +52°C
D00 | 1.3 | Max.Design Temperature | 50 °c
D00 | 1.4 | Max. Sun Temperature | + 85 °c
D00 | 1.5 | Max.Relative Humidity | 100%
D00 | 1.6 | Mean Sea Level | 12.5 m Above Sea Level
D00 | 1.7 | Seismic Factor | 0.3g
D00 | 1.8 | Max. Wind Velocity(Max) | 120 km/hr
2-General Data
D00 | 2.1 | Manufacturer | By Vendor
D00 | 2.2 | Type Number | By Vendor
D00 | 2.3 | Quantity | 1 No + 1 Set 2 Years Spare Part
D00 | 2.4 | Standard(s) | IEEE32
D00 | 2.5 | Tag Number | GCS-3.3-NGR-01
D00 | 2.6 | Applicable SLD | BK-GCS-PEDCO-120-EL-SL-0001 BK-GCS-PEDCO-120-EL-SL-0003 BK-GCS-PEDCO-120-EL-DG-0001
D00 | 2.7 | Location | Outdoor
D00 | 2.8 | Power Transformer Voltage Ratio | 11/3.45 KV
D00 | 2.9 | Power Transformer Vector Group | Dyn11
D00 | 2.10 | Resistor Element Type & Material | Grid Type Element – Stainless Steel
D00 | 2.11 | Heating Element Supporting Insulators Material | Ceramic & Porcelain
D00 | 2.12 | NGR Rated Voltage | 3.45kV / 3phase / 50Hz
D00 | 2.13 | System Phase to Neutral Voltage | 1.99kV
D00 | 2.14 | NGR Insulation Level | 3.6kV
D00 | 2.15 | Permissible Short Time Power Frequency Over Voltage | According to Clause 10.3.2 of IEEE32 Std. : 6.5 kV
D00 | 2.16 | Rated Lightning Impulse Withstand Voltage | NA for NGR
D01 | 2.17 | Short Circuit Level & Time Duration | 25 KA, 1 S
D00 | 2.18 | Required L-G Fault Current | 100 A
D00 | 2.19 | Maximum Fault Duration Time | 10 S
D00 | 2.20 | Supply Earthing System | Resistance Grounded
D00 | 2.21 | Nominal Resistance Value at 55°C | By Vendor
D00 | 2.22 | Continuous 3rd Harmonic Capacitive Current | 1A
D00 | 2.23 | Temperature Rise With Continuous Current & Worst Site Condition (55°C) | By Vendor
D00 | 2.24 | Resistance Value at -2°C | By Vendor
D00 | 2.25 | Resistance Value at 55°C | By Vendor
D00 | 2.26 | Resistance Value at 760°C | By Vendor
D00 | 2.27 | Tolerance at 20°C | By Vendor
D00 | 2.28 | Cooling Down Time Constant [S] | By Vendor
D00 | 2.29 | Final Temperature of Resistor Element After 10S | By Vendor
3.Enclosure Data
D01 | 3.1 | Enclosure Ingress Protection | IP55 With Canopy
D00 | 3.2 | Terminal Box Ingress Protection | IP 55
D00 | 3.3 | Ventilation | Air Natural
D00 | 3.4 | Enclosure Material | Hot Dip Galvanized Steel
D00 | 3.5 | Color | RAL7000 (Light Gray)
D00 | 3.6 | Enclosure Grounding Terminal | Two Sets
D00 | 3.7 | Weight of Complete Assembly [kg] | By Vendor
D00 | 3.8 | Dimension (W X D X H) [mm] | By Vendor
D01 | 3.9 | Incoming to Cable Box (from Transformers Secondary Neutral Point) | By Cable via Cable Gland from Bottom of Side Mounted Terminal Box (1×70 CU/XLPE/AWA/PVC)
D01 | 3.10 | Outgoing (Resistor to Earth) | By Bushing from Secondary Side (1×240 CU/PVC) Green-Yellow
4.Accessories Parts
D00 | 4.1 | Heater | By Vendor (PTC Type)
5. Tests
D00 | 5.1 | Routine tests
D00 |  | One Minute Power frequency Test (Acc. to IEEE32) | Witness & Report
D00 |  | Resistance measurement test at ambient temperature (Acc. to IEEE32) | Witness & Report
D00 | 5.2 | Type Test (Temperature Rise) | Certified Reports of Test on the Identical Type According to IEEE32
تسهیلات
DATA SHEETS FOR NGR
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
DT
0013
D01
بسته کاری
GCS
پروژه
BK