## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0013-D00 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0804 |  |  | Transmital Date: 11-Apr-2022
Document Title: Data Sheets For NGR |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-0804 |  |  | Transmital Date: 11-Apr-2022
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-PEDCO-120-EL-DT-0013-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | It shall be clarify, the CT for 51G will be considered in NGR or transformer. If will be considered in NGR, it shall be added and explained in data sheet and clarified by vendor. |  | BK-SUR-ENG-ELE-01-04013 | 2022-04-24 | مطابق با ردیف 9 و 10 از بند هشتم مدرک داده برگه ترانسفورماتور، اشاره شده است که ترانس نقطه نوترال توسط سازنده ترانسفورماتور تأمین خواهد شد.
2 | Page 4, Items 3.9, 3.10: Size and type of incoming and Outgoing Cables shall be added and specified. |  | BK-SUR-ENG-ELE-01-04013 | 2022-04-24 | کابل ورودی و خروجی اضافه گردید.
3 | Page 4, Item 3.1: According to electrical design criteria, enclosure ingress protection shall be modified to IP55. |  | BK-SUR-ENG-ELE-01-04013 | 2022-04-24 | تغیرات در ردیف یک از بند 3 اعمال گردید.
4 | Short circuit level and time duration shall be added and specified. |  | BK-SUR-ENG-ELE-01-04013 | 2022-04-24 | اضافه گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 24-Apr-22 |  |  |  |  | Date: