## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0010_D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0975 |  |  | Transmital Date: 21-May-2022
Document Title: Data Sheets For Power & Control Cables |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0975 |  |  | Transmital Date: 21-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DT-0010_D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | کامنت بند 2نامه شماره 443157 مورخ 1400/12/19 بقوت خود باقی ایست ،جهت طراحی تجهیزات الکتریکی براساس بند 7 مدارک الکتریکال spec پایه در بخش شرایط محیطی ملاک طراحی بدترین حالت (EXTREMES) قید شده درمدرک فرآیندی BEDDمیباشد ،لازم است دمای که دماهای ذکر شده براین اساس به 52 C˚ اصلاح گردد |  | 1401-2294-102597 | 1401-03-24 | مطابق با صحبتهای انجام شده با آن کارفرمای محترم مقرر گردید دمای تجهیزات مورد نیاز برق 52 درجه در نظر گیرد. این در حالی است که مطابق با مدارک بخش فرآیند، ماکزیمم دما 50 درجه می باشد.
2
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 29-May-22 |  |  |  |  | Date: