## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-DG-0001-D02 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0979 |  |  | Transmital Date: 21-May-2022
Document Title: Electrical Typical Schematic Diagrams For LV Panels of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0102-EL-TR-0979 |  |  | Transmital Date: 21-May-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-DG-0001-D02 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | پیرو مکاتبات قبلی کلید ورودی دیزل به کلید خانه بصورت NC در نظر گرفته شود. |  | 1401-2294-103789 | 1401-03-25 | اضافه گردید.
2 | محل انشعاب تغذیه رله PHC به قبل از کنتاگتور و بعد از سویچ فیوز جابه جا شود. |  | 1401-2294-103789 | 1401-03-25 | با توجه به اضافه نمودن MPR و دارا بودن حفاظت های ولتاژی ، رله کنترل فاز حذف گردید. چراکه در همان رله MPR وجود دارد.
3 | برای فیدرهای بزرگتر یا مساوری 30 کیلووات از رله MPR استفاده گردد. نماد مربوط به MPR نیز در Legend درج گردد. |  | 1401-2294-103789 | 1401-03-25 | رله MPR جایگزین تمامی رلهای مورد نیاز از قبیل 47، 79 و 50G گردید.
4 | پیرو بند 20شماره 00/2294/393495 مورخ 1400/11/13 چهت هرسلول می بایست یک ترانس ایزوله در نظر گرفته شود، در این مدرک جهت هر باس یک ترانس در نظر گرفته شده که می بایست اصلاح و به تعداد هر ردیف سلول(Cabicle) افزایش یابد. |  | 1401-2294-103789 | 1401-03-25 | درخواست مد نظر کارفرمای محترم به صورت نوت در صفحه 3 لحاظ شده است. لازم به ذکر است بعد از نهایی شدن قرارداد با سازنده تعداد Cubicle مشخص خواهد گردید. از اینرو با توجه به وجود این بند در نوت شماره 2، سازنده موظف به در نظر گرفتن ترانس ایزوله برای هر Cubicle خواهد بود.
5 | بند 8 نامه شماره 00//2294/393495 مورخ 1400/11/13 بقوت خود باقی است ئر این مدار در حالت تست امکان چک کردن حفاظت ها وجود ندارد. |  | 1401-2294-103789 | 1401-03-25 | برای دو تیپ موتوری M2 و M4 حفاظتهای ولتاژی و جریانی به قبل از کلید تست و سرویس انتقال پیدا کرد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 29-May-22 |  |  |  |  | Date: