## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-SL-0002-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0844 |  |  | Transmital Date: 19-Apr-2022
Document Title: Single Line Diagram For LV Switchgear of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-0844 |  |  | Transmital Date: 19-Apr-2022
[5 empty] | CRS No: NISOC-CRS-BK-SSGRL-PEDCO-110-EL-SL-0002-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | نسبت تبدیل 63/5 استاندارد نیست ، بر اساس مقادیر استاندارد 75/5 جایگزین شود. |  | 1401-2294-66366 | 1401-02-28 | اعمال گردید.
2 | استارتر یدک 75 کیلو واتی به فیدر 90 کیلو واتی جهت یدک IRP PUMP اصلاح گردد. |  | 1401-2294-66366 | 1401-02-28 | استارتر با ظرفیت 125 آمپر به استارتر 200 آمپری جهت فیدر Spare پمپ درون چاهی تبدیل گردید.
3 | لازم است که مدرک بر اساس آخرین ویرایش LOAD LIST اصلاح گردد. |  | 1401-2294-66366 | 1401-02-28 | در نامه شماره 54909 لیست بار تسهیلات سرچاهی مورد تأیید قرار گرفته است. از اینرو تمامی فیدرها بر اساس لیست بار در این مدرک لحاظ شده است.
4 | در صورت در نظر گرفته شدن الکتروپمپ جهت پر کردن مخزن آب آشامیدنی ، فیدر مربوطه در مدارک مرتبط اضافه گردد.(در این خصوص هماهنگی لازم با بخش مکانیک انجام گردد. |  | 1401-2294-66366 | 1401-02-28 | در هر زمان از پروژه که فیدری جدید توسط بخشهای دیگر مورد نیاز باشد، به این مدرک اضافه می گردد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 30-Apr-2022 |  |  |  |  | Date: