## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-SSGRL-PEDCO-110-EL-SL-0002-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0844 |  |  | Transmital Date: 19-Apr-2022
Document Title: Single Line Diagram For LV Switchgear of Well Pads |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0101-EL-TR-0844 |  |  | Transmital Date: 19-Apr-2022
[5 empty] | CRS No: PEDCO-CRS-BK-SSGRL-PEDCO-110-EL-SL-0002-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | This document shall be revised and issued as AFD after finalizing or minor comments on following documents and below mentioned comments: -Electrical Load List -Electrical Power & Control Cable Schedule Cable size, type and tag shall be added and specified for all incoming and outgoing feeders base on latest cable sizing and cable schedule. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | در هر زمان از پروژه که تغییراتی در لیست بار برق توسط بخش فرآیند به وجود آید، این مدرک به روزرسانی خواهد شد. بعد از نهایی شدن محاسبات کابل، سایز کابل در این مدرک نشان داده می شود. |  |  | Will be checked later.
2 | This document and Electrical Typical Schematic Diagrams For LV Panels of Well Pads document need to match. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | مدرک اسکماتیک و تک خطی هردو به روزرسانی شده و ارسال می گردند. |  |  | Noted and Closed.
3 | Spare feeder shall be considered base on used feeders in single line diagram from point of view size and type. (Like as basic single line diagram) |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | بر اساس لیست بار تعداد فیدرهای SPARE بروزرسانی گردیده است. |  |  | See below item 12.
4 | DGCB shall be considered fixed to provide IP55 for generator local panel. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | اعمال گردید. |  |  | Noted and Closed.
5 | Short circuit time withstand current for diesel generator LV switchgear shall be modified to 1S. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | اعمال گردید. |  |  | Noted and Closed.
6 | According to Electrical Systems Design Criteria 27R, 50BF shall be considered for incomings. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | از آنجاییکه کلید های ورودی به صورت BUILT-IN می باشد، یک نوت در مدرک اضافه شد، لازم به ذکر است در مدرک اسکماتیک حفاظت های مورد نیاز نشان داده شده است. |  |  | Noted and Closed.
7 | Current and voltage fault signal lamp shall be considered separately. Meanwhile all signal lamps descriptions shall be added. Moreover signal lamp for incoming and outgoing feeders status (ON/OFF/Fault) shall be added. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | این بند به صورت یک نوت در مدرک اضافه گردید. لازم به ذکر است فیدر های خروجی به غیر از تیپM3 فاقد حفاظت ولتاژی میباشد. |  |  | See below item 13.
8 | Emergency stop and start pushbutton shall be considered for all incoming and outgoing feeders on front of switchgear. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | این بند به صورت یک نوت در مدرک اضافه گردید. |  |  | See below item 14.
9 | Following items shall be added or modified in SLD: |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21
9-1 | 71 (Oil level) shall be added as mechanical transformer protection. Meanwhile it shall be clarify about how to activated CB by mechanical transformer protection. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | اعمال گردید. |  |  | See below item 15.
9-2 | Alarm window and related note shall be added. (This note shall be added: Alarm window shall be equipped with acknowledge and reset button.) |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | اعمال گردید. |  |  | Noted and Closed.
9-3 | Regarding there is no control system in wellhead therefore , all monitoring and controling will be done via IRP control system so type of connection (Hardwire/Serial Link) between measuring unit and IRP control system shall be based on IRP manufacturer recomendations. these item shall be added as Note. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | بعد از مشخص شدن سازنده پمپ غرقابی، نحوه ی ارتباط سیستم کنترل و فیدر مربوطه به سازنده ی تابلو های فشار ضعیف انتقال داده می شود. |  |  | Noted and Closed.
9-5 | Selector switch of incomings shall be able to show single phase voltage (added as note) |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | این بند به صورت یک نوت در مدرک اضافه گردید. |  |  | Noted and Closed.
9-6 | Frequency added in measuring unit |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | اعمال گردید. |  |  | Noted and Closed.
10 | According to telephone conversation, capacitor bank shall be deleted after getting approval from NISOC. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | بعد از اخذ تاییدیه از کارفرمای محترم، بانک خازنی حذف می گردد. |  |  | Noted and Closed.
11 | Complementary comments will be submitted after receive prerequisite and revised document. |  | BK-SUR-ENG-ELE-00-03159 | 2022-02-21 | متعاقبا اعمال می گردد. |  |  | Noted and Closed.
12 | Ref. above item 3: Despite the consultant response, Spare feeder shall be rechecked again and modified base on used feeders in single line diagram. For example 2 MCCB 200A outgoing feeders (For capacitor bank and IRP pump) has been shown in single line diagram, but MCCB 120A has been shown as spare feeder in single line diagram. |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | مطابق با فیدر خروجی 200 آمپر ، فیدر spare نیز از 120 آمپر به 200 آمپر تغییر یافت.
13 | Ref. above item 7: Despite the consultant response, the note has been mentioned only for motor type M3, it shall be shown on SLD (Like as GCS LV SLD) or modified note. Meanwhile all signal lamps descriptions shall be added. |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | در نوت شماره 15، چراغ سیگنال مجزا برای خطای ولتاژی و جریانی در نظر گرفته شده است. همچنین این چراغ ها در تک خطی تیپ M4 فیدر شماره 5 اضافه شده است. لازم به ذکر است با توجه به نوت شماره 15، سازنده موظف به در نظر گرفتن این سیگنالها به همراه توضیحات مربوطه می باشد.
14 | Ref. above item 8: According to our telephone conversation, MCCB type outgoing feeder equiped with rotary switch (For MCCB type added as note to considered in vendor document.) |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | نوت شماره 19 اضافه گردید.
15 | Ref. above item 9-1: According to our telephone conversation, mechanical transformer protections (63,71,26) shall be connected to Seperat lock out relay (Flagged and Locked Send&Receive Relay ) in LV switchgear. |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | با توجه به اینکه کلیدهای ACB تسهیلات سرچاهی به صورت Built-In می باشد، لذا حفاظت 86 درون آنها وجود دارد. ولی با توجه به نیاز پروژه یک حفاظت 86T مختص حفاظتهای ترانس قدرت در نظر گرفته شده است.
16 | According to our agreement, considered two spare feeder for type M3 and M2 are not requiered and shall be deleted. |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | فقط یک فیدر تیپ موتوری شماره 4 در نظر گرفته شده است. لازم به ذکر است با توجه به کامنت کارفرمای محترم، فیدر دیگر موتوری به فیدر Spare پمپ درون چاهی تغییر پیدا کرد.
17 | As per NISOC Comment CB in the DGCP shall be normal open and ACB in the LV switchgear shall be considered Normal Close |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | منظور گردیده است.
18 | According to NISOC comment, voltmeter and ammeter shall be considered for local generator panel. |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | با توجه به اینکه کلید ورودی از دیزل به سوییچگیر نرمالی کلوز می باشد، لذا برای تابلوی کنترل محلی دیزل و تابلوی سوییچگیر، PT و CT مجزا در نظر گرفته شده است.
19 | There is no control system in well pads to monitoring, so the considered transducer for incoming feeders can be deleted. |  | BK-SUR-ENG-ELE-01-04079 | 2022-04-30 | با توجه به عدم وجود سیستم PMS و یا DCS در تسهیلات سرچاهی، ترنسدیوسر در ورودیها حذف گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 30-Apr-2022 |  |  |  |  | Date: