## Outdoor Fix Camera
Outdoor Weather Proof IP Base Fixed Camera-1 |  |  | VENDOR REPLY
1 | Type | IP-Based, Color | IP-Based, Color
2 | Brand / Model Number | By Vendor | AXIS/P1367
3 | Material | By Vendor | Metal (zinc)
4 | Labeling | Required
5 | MTBF | 40000 hours (min) | 1/55500 s to 2 s
6 | Image Sensor Type | Day/Night, 1/3", CCD/CMOS | 1/2.9” progressive scan RGB CMOS Automatically removable infrared-cut filter
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, DNR, Auto Day/Night | IR corrected, CS-mount lens, P-Iris Varifocal 2.8–8.5 mm, F1.2 Horizontal field of view: 104°–36° Vertical field of view: 55°–20°
8 | Effective Pixel / Image Resolution | Minimum 2 Mega Pixel / (1920 x 1080 FULL HD) | 3072x1728 (5 MP) to 160x90
9 | Frame Rate | 2 MEGA PIXEL: 25 FPS (1920 x 1080 FULL HD)-30fps | 25/30 fps (50/60 Hz) in all resolutions
10 | Scanning mode | Progressive Scan | CONFIRM
11 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP | IPv4/v6, HTTP, HTTPSa, SSL/TLSa, QoS Layer 3 DiffServ, FTP, CIFS/SMB, SMTP, Bonjour, UPnP™, SNMP v1/v2c/v3 (MIB-II), DNS, DynDNS, NTP, RTSP, RTP, SFTP, TCP, UDP, IGMP, RTCP, ICMP, DHCP, ARP, SOCKS, SSH
12 | Video Compression | H.264 | H.264
13 | Lens Focal Length | 5~55mm or BETTER, Varifocal / up to 18X zoom | 5~50
14 | IR Box | 50 Meter
15 | Lens Mount | C/CS | CS
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2)
17 | Virtual PTZ | Digital PAN/Tilt/Zoom | Digital PTZ
18 | Power | 230 VAC or Power Over Ethernet | 8–28 V DC, max 8.8 W, typical 5.0 W Power over Ethernet (PoE) IEEE 802.3af/802.3at Type 1 Class 3, max 8.9 W, typical 5.0 W
19 | DNR(Digital Noise Reduction) | Yes | YES
20 | IR Cut Filter (mechanical) | Required
21 | ONVIF | Required | ONVIF® Profile S and ONVIF® Profile G
22 | Analytic image processing | Required
23 | Housing Brand / Model Number | By Vendor | VIDEOTEC/HOV32K1A100
24 | Housing Material | Aluminium | ALUMINIUM
25 | Housing Protection | Min IP65, Min IK08 | IP66/67
26 | Housing Power | 230 VAC | IN 230VAC
27 | Bracket and Installation Accessories | Required | AXIS Video Motion Detection 4, active tampering alarm, audio detection Support for AXIS Camera Application Platform enabling installation of third-party applications
28 | Housing Accessories | Heater, Fan, Double Sunshield | HEATER, FAN, SUNSHIELD
29 | Weight | By Vendor | 750 g (1.7 lb)
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 4 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Outdoor PTZ Camera
Outdoor Weather Proof IP Base PTZ Camera-1 |  |  | VENDOR REPLY
1 | Type | IP-Based, Color | IP-Based, Color
2 | Brand / Model Number | By Vendor | AXIS/Q6078
3 | Material | By Vendor | Metal casing (aluminum)
4 | Labeling | Required
5 | MTBF | 40000 hours (min) | 1/10000 s to 1 s
6 | Image Sensor Type | Day/Night, 1/4",CCD/CMOS | 1/2.5” progressive scan RGB CMOS
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, DNR, Auto Day/Night
8 | Effective Pixel / Image Resolution | Minimum 2 Mega Pixel / (1920 x 1080 FULL HD) | UHD 4K with 20x optical zoom
9 | Frame Rate | 2 MEGA PIXEL: 25 FPS (1920 x 1080 FULL HD)-30fps | Up to 25/30 fps (50/60 Hz) in 4K Up to 50/60 fps (50/60 Hz) in all other resolutions
10 | Scanning mode | Progressive Scan
11 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP | IPv4, IPv6 USGv6, ICMPv4/ICMPv6, HTTP, HTTP/2, HTTPSa, TLSa, QoS Layer 3 DiffServ, FTP, SFTP, CIFS/SMB, SMTP, mDNS (Bonjour), UPnP®, SNMP v1/v2c/v3 (MIB-II), DNS/DNSv6, DDNS, NTP, RTSP, RTP, SRTP, TCP, UDP, IGMPv1/v2/v3, RTCP, ICMP, DHCPv4/v6, ARP, SOCKS, SSH, NTCIP, LLDP, CDP, MQTT v3.1.1, Syslog, Link-Local address (ZeroConf
12 | Video Compression | H.264 | H.264
13 | optical Zoom | 36 X optical | 20X
14 | Digital Zoom | 18 X Digital | 12X
15 | IR Box | 250 Meter
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2)
17 | Virtual PTZ | Digital PAN/Tilt/Zoom | DIGITAL PTZ
18 | Power | 230 VAC | 100–240 V AC, max 66.1 W Camera consumption: typical 16 W, max 51 W
19 | DNR(Digital Noise Reduction) | Yes | YES
20 | Pan Travel | 360° Continuous | 360° endless
21 | Tilt Travel | 180° | 220°
22 | Manual Tilt Speed | 1° /SEC to 24° /SEC | 0.05°–450°/s
23 | Manual Pan Speed | 1° /SEC to 48° /SEC | 0.05°–450°/s
24 | Preset Tilt Speed | 1° /SEC to 24° /SEC | 0.05°–450°/s
25 | Preset Pan Speed | 1° /SEC to 48° /SEC | 0.05°–450°/s
26 | IR Cut Filter (mechanical) | Required | Automatically removable infrared-cut filter
27 | ONVIF | Required | ONVIF® Profile G ONVIF® Profile S and ONVIF® Profile T
28 | Analytic image processing | Required
29 | Bracket and Installation Accessories | Required
30 | Housing Accessories | Heater, Fan, Double Sunsheild, Tank 10L with pump, Telemetry receive
31 | Housing Movement | Horizental: countinuous rotation / Vertical:+45° to -20°
32 | Housing horizontal and vertical speed | 20°/S
33 | Weight | By Vendor | 3.75 kg (8.3 lb)
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 5 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Outdoor Dome Camera
Outoor IP Speed Dome Camera |  |  | VENDOR REPLY
1 | Type | IP-Based, Color | NP
2 | Brand / Model Number | By Vendor | NP
3 | Material | Required | NP
4 | MTBF | 40000 hours (min) | NP
5 | Mounting/Mounting Accessories | Ceil/Required | NP
6 | Image Sensor Type | Day/Night, 1/4",CCD/CMOS | NP
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, Auto Day/Night | NP
8 | Effective Pixel / Image Resolution | Minimum 2 Mega Pixel / (1920 x 1080 FULL HD) | NP
9 | Scanning mode | Progressive Scan | NP
10 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP | NP
11 | Stream | Min 2 full option 2 Mega Pixel: 30 fps | NP
12 | Video Compression | H264 | NP
13 | IR Box | 250 Meter | NP
14 | Protection | Min IP65 | NP
15 | Lens | VARIFOCAL | NP
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2) | NP
17 | Panning Range | 360° Continuously | NP
18 | Preset Panning Speed | More than 120° /S | NP
19 | Preset Tilting Speed | More than 80° /S | NP
20 | Zoom Ratio | Motorized Zoom,Min 30 X Optical | NP
21 | Digital Zoom Ratio | Min 18 X Digital | NP
22 | Lens | 4.3 mm to 129 mm, F/1.6 – F/4.7, autofocus | NP
23 | Image Stabilizer | Must be support | NP
24 | Alarm Input /Output | Min 2 Input/ 2 relay output | NP
25 | Power Supply/Power Consumption | 230V AC/ 24V DC/ POE | NP
26 | ONVIF | Required | NP
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 6 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Indoor Dome Camera
Indoor IP Fixed Dome Camera |  |  | VENDOR REPLY
1 | Type | IP-Based, Color | IP-Based, Color
2 | Brand / Model Number | By Vendor | AXIS/Q3617-VE
3 | Material | By Vendor | ALUMINUM
4 | MTBF | 40000 hours (min) | 1/100000 s to 2 s
5 | Mounting/Mounting Accessories | Ceil/Required | Mounting bracket with holes for junction boxes (double-gang, single-gang, 4” octagon and 4” square) and for wall or ceiling mount ¾” (M25) conduit side entries
6 | Image Sensor Type | Day/Night, 1/3",CCD/CMOS | Progressive scan RGB CMOS 1/1.8”
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, DNR, Auto Day/Night
8 | Effective Pixel / Image Resolution | (1920 x 1080 FULL HD) | 4MG
9 | Scanning mode | Progressive Scan
10 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP | IPv4, IPv6 USGv6, HTTP, HTTPSa, SSL/TLSa, QoS Layer 3 DiffServ, FTP, CIFS/SMB, SMTP, Bonjour, UPnPTM, SNMP v1/v2c/v3 (MIB-II), DNS, DynDNS, NTP, RTSP, RTP, SFTP, SRTP, TCP, UDP, IGMPv1/v2/v3, RTCP, ICMP, DHCP, ARP, SOCKS, SSH, LLDP, MQTT v3.1.1
11 | Stream | Min 2 full option 2 Mega Pixel: 30fps
12 | Video Compression | H.264, H265 | H.264
13 | Protection | Vandal Resistant, Min IP54, Min IK10 | IP66-, IP67-, IP6K9K- and NEMA 4X-rated, IK10 impact-resistant casing with polycarbonate dome.
14 | Lens Focal Length | Min 3-12 mm, VARIFOCAL | Varifocal, 4.1–9 mm, F1.6
15 | Zoom | 10 X digital
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2) | 0.15 lux at 50 IRE, F1.6; B/W: 0.03 lux at 50 IRE, F1.6
17 | Virtual PTZ | Digital PAN/Tilt/Zoom | Optical zoom and digital PTZ preset positions
18 | IR Cut Filter (mechanical) | Required | Automatically removable infrared-cut filter
19 | Power Supply/Power Consumption | 230 VAC+POE/VTA | Power over Ethernet (PoE) IEEE 802.3af/802.3at Type 1 Class 3 Typical 6.1 W, max 11.4 W
20 | ONVIF | Required | ONVIF® Profile S and ONVIF® Profile G, ONVIF® Profile T
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 7 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## License Plate Recognition
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Vehicle LPR (License Plate Recognition) System |  |  | VENDOR REPLY
1 | Image Sensor | Type : CCD or CMOS With Progressives | CMOS
2 |  | Size: 1/4" or 1/3" (VTA) | 1/3"
3 |  | Features: Day/Night, ALC, BLC, AWB, DNR | Automatically removable infrared-cut filter
4 | Power | 24v AC or POE/ AC 220V | CONFIRM
5 | Video Output | IP Ethernet Protocol | CONFIRM
6 | High shutter speed support | required | CONFIRM
7 | Image Resolution | Min 2 Mega Pixel full HD | CONFIRM
8 | IR Projector | Required(Car plate shall be read in 0.0Lux) | CONFIRM
9 | Iris | Auto Iris | CONFIRM
10 | Virtual PTZ | Yes | CONFIRM
11 | Image Compression | M-JPEG , MPEG-4 , JPEG , H-264 | CONFIRM
12 | Direct activation with ground sensor (Loop detector) | Required | CONFIRM
13 | photo taking | both Auto and Manual support | CONFIRM
14 | Image processing | Embeded or ANPR (VTA) | CONFIRM
15 | plate recognition @ Vehicle speed | Max 25 Km/h | CONFIRM
16 | WDR | 120dB with turned on light of vehicle at day and night | CONFIRM
17 | ground sensor (Loop detector) | Required | CONFIRM
18 | Trafic light | Required (Red/Green) | CONFIRM
19 | Barrier | Motorised -both Auto and Manual support | CONFIRM
20 | RFID Tag Reader | Support | CONFIRM
21 | Auto control for trafic light | Red/Green | CONFIRM
22 | Auto control for road barrier | Required | CONFIRM
23 | Data Bank for drivers and vehicles | Unlimited records and Support multiple reports | CONFIRM
24 | Software Capabilities | multi binding for drivers and plates/ definition of mutiple groups and actions for different times and groups | CONFIRM
25 | Min History Backup | 2 years | CONFIRM
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 8 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## POLE
Pole |  |  | VENDOR REPLY
1 | Type | Standard, Octagonal continuously tapered | STANDARD
2 | Brand / Model Number | By Vendor | NIKNOOR
3 | Mounting Type | Flanged Mounted | Flanged Mounted
4 | Material | ST37, Hot Dip Galvanized Steel | ST37, HDG
5 | Height(meter) | 8 meter for speed dome camera / 4 & 6 meter for fixed camera, | 8M & 4M
6 | Required Bolts and Nuts | Hot Deep Galvanized | HDG
7 | Options | Junction Box Bracket, Hole sleeve for cable entery and clamp type bracket | CONFIRM
8 | Thickness(mm) | 8 meter hieght: 8 mm 6 meter hieght: 6 mm 4 meter hieght: 4 mm | 8 meter hieght: 8 mm 6 meter hieght: 6 mm 4 meter hieght: 4 mm
9 | Plate and and brackets for installing cameras, Junction boxes, washer tanks and other accessories for cameras | Required | Plate and and brackets
10 | Hole for cables (to JB and camera) | Required | CONFIRM
11 | Plate Thickness And Other Details | As Per "Scope Of Work For Security System" | CONFIRM
12 | Max Deflection At Max Wind | 10mm | CONFIRM
13 | Lightning Protection | Required | CONFIRM
14 | Number Of Arms | As Per Related Material Requisition Document | CONFIRM
15 | Weight | By Vendor
16 | All the cabling such as power, data, earthing and lightening | Required | CONFIRM
17 | Concrete / Concrete(Megr) | min 350 /150 kg/m3 | CONFIRM
18 | Foundation dimensions (L x W x H) | 8m: Min 150 x 150 x 150 cm 6m: Min 115 x 115 x 115 cm 4m: Min 85 x 85 x 90 cm | CONFIRM
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 9 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## NVR
Network Video Recorder Server-Part 1 |  |  | VENDOR REPLY
1 | Number Of Ports | Joystick port, Additional USB port, 2 Gbps Fast Ethernet Port(1000Base-T) | Joystick port, Additional USB port, 2 Gbps Fast Ethernet Port(1000Base-T)
2 | Brand / Model Number | By Vendor | HPE/DL380 GEN10
3 | Labling | Required
4 | Mounting/ Mounting Accessories | Rack Mount/ Required | RACK MOUNT
5 | Recording Storage Capacity | Required | CONFIRM
6 | Hard Disk Drive Configuration | RAID 0,1,5,6 | 5
7 | Hard Type | Surveillance, Industrial 24*7, | CONFIRM
8 | Model | HOT PLUG | CONFIRM
9 | Hard Capacity Requirement | 2TB for per camera | CONFIRM
10 | Software with license | Required | CONFIRM
11 | Number of camera channels supports | Required | CONFIRM
12 | Recording Rate | By Vendor
13 | Operating System | Required | CONFIRM
14 | Processor | Xeon, 4GHz or higher | Xeon, 4GHz or higher
15 | Memory | Min. 2 GB DDR RAM | 3TB EITH 128 GB DDR4
16 | Video Outputs | Required | CONFIRM
17 | Optical Drive | Required | CONFIRM
18 | Form Factor | Required | CONFIRM
19 | Dimensions (LxWxH) | By Vendor | 44.55*73.03*8.74CM
20 | Weight | By Vendor | 14.76 KG
21 | Operating Temperature | Required | CONFIRM
22 | Rremote PC Client / Operating System | Required | CONFIRM
23 | Features | Min. 30 fps speed for each camera and save for 30days with FUll HD quality 2TB HDD foor each camera | CONFIRM
24 | Power Supply/ Power Consumption | 230VAC with minimum 600W redundant power supply | 2 Flexible Slot power supplies, maximum depending on model
25 | Network Adapter (NIC) | Dual TCP/ IP Integrated 10/100/1000 Base –T | CONFIRM
26 | Sound Card | In- Built | CONFIRM
27 | Graphic Card | Super VGA non-interlaced graphics card capable of 1024x768 pixel resolution and 65K colors (or true color) with 4MB video memory or better | Choice of up to 3 double wide GPGPUs, or 5 single wide GPGPUs
28 | Recording Speed | 30 fps/ channel (For all channel)-2 Mpixel | CONFIRM
29 | Keyboards | PS2 Keyboard | CONFIRM
30 | Mouse | Optical Mouse with scroll | CONFIRM
31 | Operating system | MS Windows OS or Linux (Latest versions) at the time of tender | CONFIRM
32 | Anti Virus Software | Latest software at the time of tender/ order | CONFIRM
تسهیلات
DATA SHEET FOR CCTV
شماره صفحه: 10 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## NVR-2
Network Video Recorder Server-Part 2 |  |  | VENDOR REPLY
1 | Number Of Ports | CCTV Joystick port, Additional USB port, 2 Gbps Fast Ethernet Port(1000Base-T) | NP
2 | Brand / Model Number | By Vendor | NP
3 | Labling | Required | NP
4 | Mounting/ Mounting Accessories | Rack Mount/ Required | NP
5 | Recording Storage Capacity | Required | NP
6 | Hard Disk Drive | By Vendor | NP
7 | Analytic Software | Required | NP
8 | Number of camera channels supports | By Vendor | NP
9 | Recording Rate | Required | NP
10 | Operating System | Required | NP
11 | Processor | By Vendor | NP
12 | Memory | By Vendor | NP
13 | Video Outputs | Required | NP
14 | Optical Drive | Required | NP
15 | Form Factor | Required | NP
16 | Dimensions (LxWxH) | By Vendor | NP
17 | Operating Temperature | Required | NP
18 | Rremote PC Client / Operating System | Required | NP
19 | Features | Min. 25 fps speed for each camera and save for 30days with FUll HD quality 2TB HDD foor each camera | NP
20 | Power Supply/ Power Consumption | 230VAC with minimum 600W redundant power supply | NP
21 | Network Adapter (NIC) | Dual TCP/ IP Integrated 10/100/1000 Base –T | NP
22 | Sound Card | In- Built | NP
23 | Graphic Card | Super VGA non-interlaced graphics card capable of 1024x768 pixel resolution and 65K colors (or true color) with 4MB video memory or better | NP
24 | Keyboards | USB Keyboard | NP
25 | Mouse | Optical Mouse with scroll | NP
26 | Operating system | MS Windows OS or Linux (Latest versions) at the time of tender | NP
27 | Anti Virus Software | Latest software at the time of tender/ order | NP
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 11 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Management Software
Video Management Software(VMS) |  |  | VENDOR REPLY
1 | Operating System | Windows Server 2003, 2008, 2012 Window XP, Vista, 7, 8, 10 | CONFIRM
2 | Network | Ethernet, 1 Gbit or higher recommended. | CONFIRM
3 | Hardware Requirements | x86 Platform | CONFIRM
4 | Server requirement (for 640x480 resolution) | Core i7 (6 Cores), 3 GHz, 8 GB for up to 18 channels Xeon 6 core, 3 GHz, 8 GB for up to 18 channels Xeon 12 core, 3 GHz, 16 GB for up to 36 channels (approx. 3 channels/core, suitable to add multiple CPUs per server) Supports Nvidia GPU acceleration for Face Capture & Recognition (approx. 1 channel/2 cores for Face Recognition based features) Note: For higher resolution and larger feature set consult AllGoVision | CONFIRM
5 | Frame Rate Requirement | >8 fps for Security Analytics (Perimeter Protection/Intrusion), Face Recognition >15 fps for PTZ Analytics, People Counting, Traffic features and LPR. | CONFIRM
6 | Camera Support | Supports MJPEG, H.264, MPEG4 Supports ONVIF camera, ONVIF PTZ control | CONFIRM
7 | Video Analytics Software requirment | People Counting,Reporting & Analysis,Vehicle Counting,Wrong Way Detection,Speeding and Any change Detection,License Plate Detection,Face Detection / Face Capture,Face Recognition / Verification,Auto Tracking,Ramble Detection | CONFIRM
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 12 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Video Wall (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Inustrial Video Wall |  |  | VENDOR REPLY
1 | Diagonal screen size (inch) | Minimum 46 Inch | 46 INCH
2 | Panel resolution | 1920x1080p | 1920x1080 (16:9)
3 | Size | maximum to 1212x685x102 | 1018.08mm x 572.67mm
4 | Optimum resolution | 1920 x 1080 @ 60 Hz | 1920 x 1080
5 | Brightness | 450 cd/m² | 500 cd/m2
6 | Contrast ratio (typical) | 1400:1 | 3500:01
7 | Dynamic contrast ratio | 500,000:1 | 10,000:1
8 | Response time (typical) | 8 ms | 8 ms
9 | Aspect ratio | 16:09 | CONFIRM
10 | Display colors | 1073 M | 8 bit - 16.7M
11 | Video input | DVI-D,HDMI (x2),VGA (Analog D-Sub),DisplayPort (1.2),Component (BNC x3),Composite (BNC) | HDMI1,HDMI2
12 | Video output | DisplayPort,DVI-I,VGA (via DVI-I) | CONFIRM
13 | MTBF(in Semi-light) | 100,000 hour(s) | CONFIRM
14 | Bezel thickness | Maximum 1.8 mm(as per contract) | CONFIRM
15 | Optional accessories | Edge finishing kit | CONFIRM
|  | ColourCalibrationKit | CONFIRM
|  | HDBaseT OPS Receiver | CONFIRM
|  | IR Light Motion Sensor | CONFIRM
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 13 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Video Wall Controller (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Video Wall Controller System
| Hardware |  | VENDOR REPLY
1 | CPU | Intel® i5 6-core 2.9GHz | CONFIRM
2 | SSD | 1x 500GB SSD Optional: 2 x 500GB SSD RAID1 | CONFIRM
3 | Backplane | 4x Slot PCI Express x16 | CONFIRM
4 | Network | 1x 10GbE + 1x 1GbE | CONFIRM
5 | Case | 19” 4RU case | CONFIRM
6 | Power Supply | 230 VAC | CONFIRM
7 | MTBF | 100,000hrs | CONFIRM
Software
8 | OS | Windows, 64 Bit | CONFIRM
9 | Recovery | Easy backup and recovery USB | CONFIRM
10 | Max number of outputs | Up to 12x | CONFIRM
11 | Configuration | High End NVIDIA Quadro GPU with 4x outputs per card / Max. 32,768x32,768 pixel per system | CONFIRM
12 | Resolution | VS-2-4HO card: HDMI 2.0, 4x 4096x2160@60Hz per card VS-2-4DO card: DisplayPort 1.4, 4x 5120x3200@60Hz per card | CONFIRM
13 | Desplayy Input Port 1.2 | Up to 6x | CONFIRM
14 | HDMI 1.4 | Up to 12x | CONFIRM
15 | SDI | 6x3G and 6x12G | CONFIRM
16 | Stream Format | Protocols: RTSP, RTP, MPEG-2-TS, SRT; Distribution: unicast & multicast; Codec: H.264 (MPEG-4 Part 10 AVC) up to Level 5.2; Profiles: Baseline, Main, High, High 10, High 4:2:2, High 4:4:4 Predictive Profile Separate Plane | CONFIRM
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 14 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## industrial desktop Monitor
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Industrial LED Monitor (Desktop Monitor) |  |  | VENDOR REPLY
1 | Display Resolution | Full HD (1920 × 1080 Pixel ) | 1920X1080
2 | Size | 22 inch to 25 inch | 22
3 | Viewing Angle | H 160º / V 160º | 170°/160°
4 | Display Technology | IPS | CONFIRM
5 | MTBF | >30,000 h | CONFIRM
6 | Response Time | <9 ms | 5 ms
7 | Aspect Ratio | 16:09 | 16:09
8 | Contrast Ratio | 1000:01 | 1000:1(Typ.), 700:1(Min)
9 | Brightness | >=300 cd/m² | 250cd/m2
10 | Pixel Pitch | <0.4 mm | CONFIRM
11 | Ambient Light Sensor | Automatic | CONFIRM
12 | Input Voltage | 220 VAC | CONFIRM
13 | Inputs | DVI , RGB(HD15),BNC(for analog cctv), SVIDEO, RJ45,HDMI
14 | Panel Life Time cycle | 24/7 ( 24 Hour in 7 Day in Week) | 24/7
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 15 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Switch
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Industrial Outdoor Switch |  |  | VENDOR REPLY
1 | 10/100BASE (RJ-45 Connector) Ports | 4 or 8 | 8P
2 | 1000BASE (SFP) Ports | Min 2 | 2
3 | GLC type | SM (single mode) and the single strand bidirectional | SM
4 | Boud rate | 100/1000 | 100/1000
5 | Body material | Metal | METAL
6 | POE Mode | HPOE Support-Ring Support | POE
7 | Operation Temperature Range | According to Climate Data(Maximum 70 C) | CONFIRM
8 | Network Layer | 2 Layers | 2
9 | Config status | Secure Configable with Command Prompt
10 | Power | 220-230 VAC | CONFIRM
11 | Other Featchres | Modular | Modular
Rack Mounted Netweork Switch
12 | 10/100/1000 BASE (RJ-45 Connector) Ports | 24 or 48 | 24P
13 | 1000BASE (SFP) Ports | Minimum 12 SFP | 12 SFP
14 | GLC type | SM (single mode) and the single strand bidirectional | SM
15 | Boud rate | 100/1000 | 100/1000
16 | Body material | Metal | METAL
17 | POE Mode | Support, also Ring Support | CONFIRM
18 | Operation Temperature Range | 0° to 40° C | CONFIRM
19 | Network Layer | 2 & 3 | 2
20 | Config status | Secure Configable with Command Prompt | CONFIRM
21 | Power | 220-230 VAC | CONFIRM
22 | Other Featchres | Modular and Rackmount | Rackmount
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 16 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Intercom-Rack
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Outdoor Intercom |  |  | VENDOR REPLY
1 | Certificate | Ul,EN, | CONFIRM
2 | operating Temperature | up to 70C | up to 70C
3 | Humidity | minimum 95% | CONFIRM
4 | capability to record | Yes | YES
5 | Remote monitoring | Yes | YES
6 | Direct Access and dynamic Keys & LEDs | Yes | YES
7 | Alarm features | Pre Recordded Alarm Tones, Pre ecorded Speech Messages, Capability to Route Audio to Individually controlled Zones, Scheduled Events | CONFIRM
8 | Nerwork Protocols | IPv4, SIP, TCP, UDP,HTTPS,TFTP, RTP,DHCP,SNMP,NTP | CONFIRM
9 | ingress Protection | minimum IP66 | IP66
10 | IK rating | minimum IK08 | CONFIRM
11 | corrosion-resistant,salty mist | Yes, According to EN60945 | YES
13 | UV-resistant | yes | YES
14 | EMC | Yes, According to CE and FCC rules | YES
15 | Active Noise reduction | yes | YES
16 | adjustable microphone sensitivity and volume | yes | YES
17 | Capability of working serverless | yes | YES
CCTV Cabinet
18 | ingress Protection | IP 42 | IP42
19 | Accessories | Fan, ligth , heater , earth bar , fuse ,Power Socket(8 Port) | Fan, ligth , heater , earth bar , fuse ,Power Socket(8 Port)
20 | Door Lock | Required | YES
21 | Ral | 7035 | 7035
22 | Size | 19" ,Minimum 42 Unit | 19" ,Minimum 42 Unit
23 | Type | Movable with wheel | YES
24 | Temprature Desplay | Required | YES
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 17 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Desktop Call Station
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Desktop Call Station(With Neck swan mic) |  |  | VENDOR REPLY
1 | Type of Installation | Desk Mount | NP.
2 | Number of keys | >16
3 | Brand / Model Number | By Vendor
4 | Labling | By Vendor
5 | Material | By Vendor
6 | Protection index | Min. IP20
7 | Type of Installation | Desk Mount
8 | Power | 230 VAC, 50 Hz
9 | Site and Zone Selection | YES (One / Many / Pre-Defined Group / All)
10 | Noise-Canceling Microphone | Required
11 | Routine Speed Press-to-Talk Switch | Required
13 | Dual action "Emergency Speed" Push Button | Required
14 | Dual Action Latching Manual Alarm | Required
15 | Push Buttons (for each alarm type) | Required
16 | "Access Granted" Indicator | Required
17 | Broadcast Area-Selected Indicators | Required
18 | System 'Busy' or 'In Use' Indication | Required
19 | System 'Healthy' Indication | Required
20 | Selected and Playback of Pre-recorded Speech Message | Required
21 | Power Fail Indication | Required
22 | Local control station visual alarm | Required
23 | System monitoring equipment | Required
24 | Keyboard and Microphone | Required
25 | Control and zone selection circuitry | Required
26 | Number of keys | >16
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 18 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## CCTV Client Software
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
CCTV Client Harsware |  |  | VENDOR REPLY
1 | Operating System | Windows 10 Pro 64-bit | Windows 10 Pro 64-bit
2 | CPU | Intel® Core i5, such as Intel® Core i5-8500 | COREI5
3 | RAM | 8GB, DDR4-2666 MHz | 8GB
4 | Graphic card | Intel® HD Graphics 630 | Intel® HD Graphics 630
5 | Network | 1 Gbps | 1
CCTV Client Software
7 | Control and view Minium 4 camera feeds simultaneously on 22 inch | Required | CONFIRM
8 | Use IP cameras as well | Required | CONFIRM
9 | Pan/Tilt/Zoom (PTZ) support for many network cameras | Required | CONFIRM
10 | Digitally zoom, even if your camera does not support it | Required | CONFIRM
11 | Adjust the orientation of live feeds | Required | CONFIRM
12 | View cameras on Multiple Monitors | Required | CONFIRM
13 | Capture JPEG, MJPEG, MPEG-4 and H.264 stream from IP cameras | Support | CONFIRM
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 19 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK