## Indoor Dome Camera
Indoor IP Fixed Dome Camera |  |  | VENDOR REPLY
1 | Type | IP-Based, Color | IP-Based, Color
2 | Brand / Model Number | By Vendor | Avigilon-2.0 C H5A-D1
3 | Material | By Vendor
4 | MTBF | 40000 hours (min) | Included
5 | Mounting/Mounting Accessories | Ceil/Required | Included
6 | Image Sensor Type | Day/Night, 1/3",CCD/CMOS | 1/2.8” progressive scan CMOS
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, DNR, Auto Day/Night | Auto Iris, WDR, Auto Day/Night
8 | Effective Pixel / Image Resolution | (1920 x 1080 FULL HD) | Included
9 | Scanning mode | Progressive Scan | 30 fps
10 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP | Included
11 | Stream | Min 2 full option 2 Mega Pixel: 30fps | Included
12 | Video Compression | H.264, H265 | Included
13 | Protection | Vandal Resistant, Min IP54, Min IK10 | IP66
14 | Lens Focal Length | Min 3-12 mm, VARIFOCAL | 3.3 - 9 mm
15 | Zoom | 10 X digital | Included
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2) | 0.027 lux in color mode, 0.014 lux in monochrome mode, 0 lux with IR
17 | Virtual PTZ | Digital PAN/Tilt/Zoom | Included
18 | IR Cut Filter (mechanical) | Required | Included
19 | Power Supply/Power Consumption | 230 VAC+POE/VTA | VDC: 12 V ± 10%, 12 W min / VAC: 24 V ± 10%, 13 VA min / PoE: IEEE802.3af Class 3 compliant
20 | ONVIF | Required | Included
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 7 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Outdoor Fix Camera
Outdoor Weather Proof IP Base Fixed Camera-1 |  |  | VENDOR REPLY
1 | Type | IP-Based, Color | IP-Based, Color
2 | Brand / Model Number | By Vendor | Avigilo / 2.0 C-H5A-B1
3 | Material | By Vendor
4 | Labeling | Required | Included
5 | MTBF | 40000 hours (min) | Included
6 | Image Sensor Type | Day/Night, 1/3", CCD/CMOS | 1/2.8” progressive scan CMOS
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, DNR, Auto Day/Night | Auto Iris, WDR, Auto Day/Night
8 | Effective Pixel / Image Resolution | Minimum 2 Mega Pixel / (1920 x 1080 FULL HD) | Minimum 2 Mega Pixel / (1920 x 1080 FULL HD)
9 | Frame Rate | 2 MEGA PIXEL: 25 FPS (1920 x 1080 FULL HD)-30fps | Included
10 | Scanning mode | Progressive Scan | Included
11 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP | Included
12 | Video Compression | H.264 | Included
13 | Lens Focal Length | 5~55mm or BETTER, Varifocal / up to 18X zoom | 4.7 - 84.6 mm
14 | IR Box | 50 Meter | Included
15 | Lens Mount | C/CS | Included
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2) | 0.027 lux in color mode, 0.014 lux in monochrome mode, 0 lux with IR
17 | Virtual PTZ | Digital PAN/Tilt/Zoom | Not Applicable
18 | Power | 230 VAC or Power Over Ethernet | VDC: 12 V ± 10%, 7 W min VAC: 24 V ± 10%, 9 VA min PoE: IEEE802.3af Class 3 compliant
19 | DNR(Digital Noise Reduction) | Yes | Included
20 | IR Cut Filter (mechanical) | Required | Included
21 | ONVIF | Required | Included
22 | Analytic image processing | Required | Included
23 | Housing Brand / Model Number | By Vendor | Videotec-HOV32K1A000
24 | Housing Material | Aluminium | Included
25 | Housing Protection | Min IP65, Min IK08 | IP66-67 / IK10
26 | Housing Power | 230 VAC | Included
27 | Bracket and Installation Accessories | Required | Included
28 | Housing Accessories | Heater, Fan, Double Sunshield | Included
29 | Weight | By Vendor | 3 Kg (Housing)
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 4 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Outdoor PTZ Camera
Outdoor Weather Proof IP Base PTZ Camera-1 |  |  | VENDOR REPLY
1 | Type | IP-Based, Color | Included
2 | Brand / Model Number | By Vendor | Avigilon / 2.0 C-H4IR PTZ-DP30
3 | Material | By Vendor | As Attached Datasheet
4 | Labeling | Required | Included
5 | MTBF | 40000 hours (min) | Included
6 | Image Sensor Type | Day/Night, 1/4",CCD/CMOS | 1/2.8” progressive scan CMOS
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, DNR, Auto Day/Night | Included
8 | Effective Pixel / Image Resolution | Minimum 2 Mega Pixel / (1920 x 1080 FULL HD) | Included
9 | Frame Rate | 2 MEGA PIXEL: 25 FPS (1920 x 1080 FULL HD)-30fps | Included
10 | Scanning mode | Progressive Scan | Included
11 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP | Included
12 | Video Compression | H.264 | Included
13 | optical Zoom | 36 X optical | 30 X
14 | Digital Zoom | 18 X Digital | 100 X
15 | IR Box | 250 Meter | Included
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2) | 0 lux in IR mode; 0.1 lux (F/1.6) in color mode (no IR); 0.03 lux (F/1.6) in monochrome mode (no IR)
17 | Virtual PTZ | Digital PAN/Tilt/Zoom | Included
18 | Power | 230 VAC | Included
19 | DNR(Digital Noise Reduction) | Yes | Included
20 | Pan Travel | 360° Continuous | Included
21 | Tilt Travel | 180° | Included
22 | Manual Tilt Speed | 1° /SEC to 24° /SEC | Included
23 | Manual Pan Speed | 1° /SEC to 48° /SEC | Included
24 | Preset Tilt Speed | 1° /SEC to 24° /SEC | Included
25 | Preset Pan Speed | 1° /SEC to 48° /SEC | Included
26 | IR Cut Filter (mechanical) | Required | Included
27 | ONVIF | Required | Included
28 | Analytic image processing | Required | Not Included
29 | Bracket and Installation Accessories | Required | Included
30 | Housing Accessories | Heater, Fan, Double Sunsheild, Tank 10L with pump, Telemetry receive | Included
31 | Housing Movement | Horizental: countinuous rotation / Vertical:+45° to -20° | Included
32 | Housing horizontal and vertical speed | 20°/S | Included
33 | Weight | By Vendor | 6.6 Kg
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 5 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## POLE
Pole |  |  | VENDOR REPLY
1 | Type | Standard, Octagonal continuously tapered | Included
2 | Brand / Model Number | By Vendor | Ehdas Gostar
3 | Mounting Type | Flanged Mounted | Included
4 | Material | ST37, Hot Dip Galvanized Steel | Included
5 | Height(meter) | 8 meter for speed dome camera / 4 & 6 meter for fixed camera, | Included
6 | Required Bolts and Nuts | Hot Deep Galvanized | Included
7 | Options | Junction Box Bracket, Hole sleeve for cable entery and clamp type bracket | Included
8 | Thickness(mm) | 8 meter hieght: 8 mm 6 meter hieght: 6 mm 4 meter hieght: 4 mm | Included
9 | Plate and and brackets for installing cameras, Junction boxes, washer tanks and other accessories for cameras | Required | Included
10 | Hole for cables (to JB and camera) | Required | Included
11 | Plate Thickness And Other Details | As Per "Scope Of Work For Security System" | Included
12 | Max Deflection At Max Wind | 10mm | Included
13 | Lightning Protection | Required | Included
14 | Number Of Arms | As Per Related Material Requisition Document | Included
15 | Weight | By Vendor | Included
16 | All the cabling such as power, data, earthing and lightening | Required | Included
17 | Concrete / Concrete(Megr) | min 350 /150 kg/m3 | Included
18 | Foundation dimensions (L x W x H) | 8m: Min 150 x 150 x 150 cm 6m: Min 115 x 115 x 115 cm 4m: Min 85 x 85 x 90 cm | Included
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 9 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## NVR
Network Video Recorder Server-Part 1 |  |  | VENDOR REPLY
1 | Number Of Ports | Joystick port, Additional USB port, 2 Gbps Fast Ethernet Port(1000Base-T) | Included
2 | Brand / Model Number | By Vendor | Dl380 HP-Gen10
3 | Labling | Required | Included
4 | Mounting/ Mounting Accessories | Rack Mount/ Required | Included
5 | Recording Storage Capacity | Required | Included
6 | Hard Disk Drive Configuration | RAID 0,1,5,6 | Included
7 | Hard Type | Surveillance, Industrial 24*7, | Included
8 | Model | HOT PLUG | Included
9 | Hard Capacity Requirement | 2TB for per camera | Included
10 | Software with license | Required | Included
11 | Number of camera channels supports | Required | 128
12 | Recording Rate | By Vendor | 100Mb/s
13 | Operating System | Required | Windows
14 | Processor | Xeon, 4GHz or higher | Included
15 | Memory | Min. 2 GB DDR RAM | Included
16 | Video Outputs | Required | Included
17 | Optical Drive | Required | Included
18 | Form Factor | Required | It will be submited
19 | Dimensions (LxWxH) | By Vendor | As Attached datasheet
20 | Weight | By Vendor | As Attached datasheet
21 | Operating Temperature | Required | As Attached datasheet
22 | Rremote PC Client / Operating System | Required | Windows
23 | Features | Min. 30 fps speed for each camera and save for 30days with FUll HD quality 2TB HDD foor each camera | Included
24 | Power Supply/ Power Consumption | 230VAC with minimum 600W redundant power supply | As Attached datasheet
25 | Network Adapter (NIC) | Dual TCP/ IP Integrated 10/100/1000 Base –T | Included
26 | Sound Card | In- Built | Included
27 | Graphic Card | Super VGA non-interlaced graphics card capable of 1024x768 pixel resolution and 65K colors (or true color) with 4MB video memory or better | Included
28 | Recording Speed | 30 fps/ channel (For all channel)-2 Mpixel | Included
29 | Keyboards | PS2 Keyboard | Included
30 | Mouse | Optical Mouse with scroll | Included
31 | Operating system | MS Windows OS or Linux (Latest versions) at the time of tender | Included
32 | Anti Virus Software | Latest software at the time of tender/ order | Included
تسهیلات
DATA SHEET FOR CCTV
شماره صفحه: 10 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Management Software
Video Management Software(VMS) |  |  | VENDOR REPLY
1 | Operating System | Windows Server 2003, 2008, 2012 Window XP, Vista, 7, 8, 10 | Windows Server 2003
2 | Network | Ethernet, 1 Gbit or higher recommended. | Included
3 | Hardware Requirements | x86 Platform | Included
4 | Server requirement (for 640x480 resolution) | Core i7 (6 Cores), 3 GHz, 8 GB for up to 18 channels Xeon 6 core, 3 GHz, 8 GB for up to 18 channels Xeon 12 core, 3 GHz, 16 GB for up to 36 channels (approx. 3 channels/core, suitable to add multiple CPUs per server) Supports Nvidia GPU acceleration for Face Capture & Recognition (approx. 1 channel/2 cores for Face Recognition based features) Note: For higher resolution and larger feature set consult AllGoVision | Included
5 | Frame Rate Requirement | >8 fps for Security Analytics (Perimeter Protection/Intrusion), Face Recognition >15 fps for PTZ Analytics, People Counting, Traffic features and LPR. | Included
6 | Camera Support | Supports MJPEG, H.264, MPEG4 Supports ONVIF camera, ONVIF PTZ control | Included
7 | Video Analytics Software requirment | People Counting,Reporting & Analysis,Vehicle Counting,Wrong Way Detection,Speeding and Any change Detection,License Plate Detection,Face Detection / Face Capture,Face Recognition / Verification,Auto Tracking,Ramble Detection | Included
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 12 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Video Wall Controller (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Video Wall Controller System
| Hardware |  | VENDOR REPLY
1 | CPU | Intel® i5 6-core 2.9GHz | Included
2 | SSD | 1x 500GB SSD Optional: 2 x 500GB SSD RAID1 | Included
3 | Backplane | 4x Slot PCI Express x16 | Included
4 | Network | 1x 10GbE + 1x 1GbE | Included
5 | Case | 19” 4RU case | Included
6 | Power Supply | 230 VAC | Included
7 | MTBF | 100,000hrs | 60,000 hrs
Software
8 | OS | Windows, 64 Bit | Included
9 | Recovery | Easy backup and recovery USB | Included
10 | Max number of outputs | Up to 12x | Included
11 | Configuration | High End NVIDIA Quadro GPU with 4x outputs per card / Max. 32,768x32,768 pixel per system | Included
12 | Resolution | VS-2-4HO card: HDMI 2.0, 4x 4096x2160@60Hz per card VS-2-4DO card: DisplayPort 1.4, 4x 5120x3200@60Hz per card | Resolutions: 1024*768, 1920*1080
13 | Desplayy Input Port 1.2 | Up to 6x | Included
14 | HDMI 1.4 | Up to 12x | Included
15 | SDI | 6x3G and 6x12G | Not Included
16 | Stream Format | Protocols: RTSP, RTP, MPEG-2-TS, SRT; Distribution: unicast & multicast; Codec: H.264 (MPEG-4 Part 10 AVC) up to Level 5.2; Profiles: Baseline, Main, High, High 10, High 4:2:2, High 4:4:4 Predictive Profile Separate Plane | Supported
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 14 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Video Wall (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Inustrial Video Wall |  |  | VENDOR REPLY
1 | Diagonal screen size (inch) | Minimum 46 Inch | Included
2 | Panel resolution | 1920x1080p | Included
3 | Size | maximum to 1212x685x102 | Included
4 | Optimum resolution | 1920 x 1080 @ 60 Hz | Included
5 | Brightness | 450 cd/m² | Included
6 | Contrast ratio (typical) | 1400:1 | Included
7 | Dynamic contrast ratio | 500,000:1 | Included
8 | Response time (typical) | 8 ms | Included
9 | Aspect ratio | 16:09 | Included
10 | Display colors | 1073 M | Included
11 | Video input | DVI-D,HDMI (x2),VGA (Analog D-Sub),DisplayPort (1.2),Component (BNC x3),Composite (BNC) | Included
12 | Video output | DisplayPort,DVI-I,VGA (via DVI-I) | Included
13 | MTBF(in Semi-light) | 100,000 hour(s) | 50000 hour(s)
14 | Bezel thickness | Maximum 1.8 mm(as per contract) | Included
15 | Optional accessories | Edge finishing kit | ….
|  | ColourCalibrationKit | ….
|  | HDBaseT OPS Receiver | ….
|  | IR Light Motion Sensor | ….
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 13 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## industrial desktop Monitor
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Industrial LED Monitor (Desktop Monitor) |  |  | VENDOR REPLY
1 | Display Resolution | Full HD (1920 × 1080 Pixel ) | Included
2 | Size | 22 inch to 25 inch | Included
3 | Viewing Angle | H 160º / V 160º | Included
4 | Display Technology | IPS | LED flat-Screen panel
5 | MTBF | >30,000 h | Included
6 | Response Time | <9 ms | 5 ms
7 | Aspect Ratio | 16:09 | Included
8 | Contrast Ratio | 1000:01 | Included
9 | Brightness | >=300 cd/m² | Included
10 | Pixel Pitch | <0.4 mm | Included
11 | Ambient Light Sensor | Automatic | Included
12 | Input Voltage | 220 VAC | Included
13 | Inputs | DVI , RGB(HD15),BNC(for analog cctv), SVIDEO, RJ45,HDMI | HDMI, DVI-D, and VGA
14 | Panel Life Time cycle | 24/7 ( 24 Hour in 7 Day in Week) | Included
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 15 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Switch
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Industrial Outdoor Switch |  |  | VENDOR REPLY
1 | 10/100BASE (RJ-45 Connector) Ports | 4 or 8 | 8 Port
2 | 1000BASE (SFP) Ports | Min 2 | Included
3 | GLC type | SM (single mode) and the single strand bidirectional | Included
4 | Boud rate | 100/1000 | Included
5 | Body material | Metal | Included
6 | POE Mode | HPOE Support-Ring Support | Included
7 | Operation Temperature Range | According to Climate Data(Maximum 70 C) | from -40 up to +75 °C
8 | Network Layer | 2 Layers | Layer 2
9 | Config status | Secure Configable with Command Prompt | Included
10 | Power | 220-230 VAC | Included
11 | Other Featchres | Modular | Included
Rack Mounted Netweork Switch
12 | 10/100/1000 BASE (RJ-45 Connector) Ports | 24 or 48 | Included
13 | 1000BASE (SFP) Ports | Minimum 12 SFP | Included
14 | GLC type | SM (single mode) and the single strand bidirectional | Included
15 | Boud rate | 100/1000 | Included
16 | Body material | Metal | Included
17 | POE Mode | Support, also Ring Support | Included
18 | Operation Temperature Range | 0° to 40° C | Included
19 | Network Layer | 2 & 3 | 2 & 3
20 | Config status | Secure Configable with Command Prompt | Included
21 | Power | 220-230 VAC | Included
22 | Other Featchres | Modular and Rackmount | Included
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 16 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Intercom-Rack
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Outdoor Intercom |  |  | VENDOR REPLY
1 | Certificate | Ul,EN, | IEC/UL62368-1, EN61000-6-X, EN60945, EN 50121-4; In order to comply with UL safety requirements, the unit has to be supplied by a power supply specified as a Limited Power Source (LPS) or PS2 (cased on IEC/UL 62368-1 definition) or NEC Class 2 source of supply
2 | operating Temperature | up to 70C | Included
3 | Humidity | minimum 95% | Included
4 | capability to record | Yes | Included
5 | Remote monitoring | Yes | Included
6 | Direct Access and dynamic Keys & LEDs | Yes | Included
7 | Alarm features | Pre Recordded Alarm Tones, Pre ecorded Speech Messages, Capability to Route Audio to Individually controlled Zones, Scheduled Events | Included
8 | Nerwork Protocols | IPv4, SIP, TCP, UDP,HTTPS,TFTP, RTP,DHCP,SNMP,NTP | Included
9 | ingress Protection | minimum IP66 | Included
10 | IK rating | minimum IK08 | Included
11 | corrosion-resistant,salty mist | Yes, According to EN60945 | Included
13 | UV-resistant | yes | Included
14 | EMC | Yes, According to CE and FCC rules | Included
15 | Active Noise reduction | yes | Included
16 | adjustable microphone sensitivity and volume | yes | Included
17 | Capability of working serverless | yes | Included
CCTV Cabinet
18 | ingress Protection | IP 42 | Included
19 | Accessories | Fan, ligth , heater , earth bar , fuse ,Power Socket(8 Port) | Included
20 | Door Lock | Required | Included
21 | Ral | 7035 | Included
22 | Size | 19" ,Minimum 42 Unit | Included
23 | Type | Movable with wheel | Included
24 | Temprature Desplay | Required | Included
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 17 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## CCTV Client Software
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
CCTV Client Harsware |  |  | VENDOR REPLY
1 | Operating System | Windows 10 Pro 64-bit | Included
2 | CPU | Intel® Core i5, such as Intel® Core i5-8500 | Included
3 | RAM | 8GB, DDR4-2666 MHz | Included
4 | Graphic card | Intel® HD Graphics 630 | Included
5 | Network | 1 Gbps | Included
CCTV Client Software
7 | Control and view Minium 4 camera feeds simultaneously on 22 inch | Required | Included
8 | Use IP cameras as well | Required | Included
9 | Pan/Tilt/Zoom (PTZ) support for many network cameras | Required | Included
10 | Digitally zoom, even if your camera does not support it | Required | Included
11 | Adjust the orientation of live feeds | Required | Included
12 | View cameras on Multiple Monitors | Required | Included
13 | Capture JPEG, MJPEG, MPEG-4 and H.264 stream from IP cameras | Support | Included
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 19 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK