## Outdoor Fix Camera
Outdoor Weather Proof IP Base Fixed Camera-1 |  |  | VENDOR REPLY
1 | Type | IP-Based, Color
2 | Brand / Model Number | By Vendor
3 | Material | By Vendor
4 | Labeling | Required
5 | MTBF | 40000 hours (min)
6 | Image Sensor Type | Day/Night, 1/3", CCD/CMOS
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, DNR, Auto Day/Night
8 | Effective Pixel / Image Resolution | Minimum 2 Mega Pixel / (1920 x 1080 FULL HD)
9 | Frame Rate | 2 MEGA PIXEL: 25 FPS (1920 x 1080 FULL HD)-30fps
10 | Scanning mode | Progressive Scan
11 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP
12 | Video Compression | H.264
13 | Lens Focal Length | 5~55mm or BETTER, Varifocal / up to 18X zoom
14 | IR Box | 50 Meter
15 | Lens Mount | C/CS
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2)
17 | Virtual PTZ | Digital PAN/Tilt/Zoom
18 | Power | 230 VAC or Power Over Ethernet
19 | DNR(Digital Noise Reduction) | Yes
20 | IR Cut Filter (mechanical) | Required
21 | ONVIF | Required
22 | Analytic image processing | Required
23 | Housing Brand / Model Number | By Vendor
24 | Housing Material | Aluminium
25 | Housing Protection | Min IP65, Min IK08
26 | Housing Power | 230 VAC
27 | Bracket and Installation Accessories | Required
28 | Housing Accessories | Heater, Fan, Double Sunshield
29 | Weight | By Vendor
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 4 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Outdoor PTZ Camera
Outdoor Weather Proof IP Base PTZ Camera-1 |  |  | VENDOR REPLY
1 | Type | IP-Based, Color
2 | Brand / Model Number | By Vendor
3 | Material | By Vendor
4 | Labeling | Required
5 | MTBF | 40000 hours (min)
6 | Image Sensor Type | Day/Night, 1/4",CCD/CMOS
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, DNR, Auto Day/Night
8 | Effective Pixel / Image Resolution | Minimum 2 Mega Pixel / (1920 x 1080 FULL HD)
9 | Frame Rate | 2 MEGA PIXEL: 25 FPS (1920 x 1080 FULL HD)-30fps
10 | Scanning mode | Progressive Scan
11 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP
12 | Video Compression | H.264
13 | optical Zoom | 36 X optical
14 | Digital Zoom | 18 X Digital
15 | IR Box | 250 Meter
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2)
17 | Virtual PTZ | Digital PAN/Tilt/Zoom
18 | Power | 230 VAC
19 | DNR(Digital Noise Reduction) | Yes
20 | Pan Travel | 360° Continuous
21 | Tilt Travel | 180°
22 | Manual Tilt Speed | 1° /SEC to 24° /SEC
23 | Manual Pan Speed | 1° /SEC to 48° /SEC
24 | Preset Tilt Speed | 1° /SEC to 24° /SEC
25 | Preset Pan Speed | 1° /SEC to 48° /SEC
26 | IR Cut Filter (mechanical) | Required
27 | ONVIF | Required
28 | Analytic image processing | Required
29 | Bracket and Installation Accessories | Required
30 | Housing Accessories | Heater, Fan, Double Sunsheild, Tank 10L with pump, Telemetry receive
31 | Housing Movement | Horizental: countinuous rotation / Vertical:+45° to -20°
32 | Housing horizontal and vertical speed | 20°/S
33 | Weight | By Vendor
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 5 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Outdoor Dome Camera
Outoor IP Speed Dome Camera |  |  | VENDOR REPLY
1 | Type | IP-Based, Color
2 | Brand / Model Number | By Vendor
3 | Material | Required
4 | MTBF | 40000 hours (min)
5 | Mounting/Mounting Accessories | Ceil/Required
6 | Image Sensor Type | Day/Night, 1/4",CCD/CMOS
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, Auto Day/Night
8 | Effective Pixel / Image Resolution | Minimum 2 Mega Pixel / (1920 x 1080 FULL HD)
9 | Scanning mode | Progressive Scan
10 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP
11 | Stream | Min 2 full option 2 Mega Pixel: 30 fps
12 | Video Compression | H264
13 | IR Box | 250 Meter
14 | Protection | Min IP65
15 | Lens | VARIFOCAL
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2)
17 | Panning Range | 360° Continuously
18 | Preset Panning Speed | More than 120° /S
19 | Preset Tilting Speed | More than 80° /S
20 | Zoom Ratio | Motorized Zoom,Min 30 X Optical
21 | Digital Zoom Ratio | Min 18 X Digital
22 | Lens | 4.3 mm to 129 mm, F/1.6 – F/4.7, autofocus
23 | Image Stabilizer | Must be support
24 | Alarm Input /Output | Min 2 Input/ 2 relay output
25 | Power Supply/Power Consumption | 230V AC/ 24V DC/ POE
26 | ONVIF | Required
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 6 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Indoor Dome Camera
Indoor IP Fixed Dome Camera |  |  | VENDOR REPLY
1 | Type | IP-Based, Color
2 | Brand / Model Number | By Vendor
3 | Material | By Vendor
4 | MTBF | 40000 hours (min)
5 | Mounting/Mounting Accessories | Ceil/Required
6 | Image Sensor Type | Day/Night, 1/3",CCD/CMOS
7 | Light Functions | AGC, ALC, Auto Iris, BLC, WDR(90db), AWB, DNR, Auto Day/Night
8 | Effective Pixel / Image Resolution | (1920 x 1080 FULL HD)
9 | Scanning mode | Progressive Scan
10 | Supported Protocols | TCP/IP, UDP/IP, HTTP, FTP, SMTP, DHCP, DNS, DDNS, NTP, SNMP, RTP
11 | Stream | Min 2 full option 2 Mega Pixel: 30fps
12 | Video Compression | H.264, H265
13 | Protection | Vandal Resistant, Min IP54, Min IK10
14 | Lens Focal Length | Min 3-12 mm, VARIFOCAL
15 | Zoom | 10 X digital
16 | Sensitivity | Color < 0.5 Lux (t=1/30 S, F=1.2) / B/W< 0.1 Lux (t=1/30 S, F=1.2)
17 | Virtual PTZ | Digital PAN/Tilt/Zoom
18 | IR Cut Filter (mechanical) | Required
19 | Power Supply/Power Consumption | 230 VAC+POE/VTA
20 | ONVIF | Required
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 7 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## License Plate Recognition
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Vehicle LPR (License Plate Recognition) System |  |  | VENDOR REPLY
1 | Image Sensor | Type : CCD or CMOS With Progressives
2 |  | Size: 1/4" or 1/3" (VTA)
3 |  | Features: Day/Night, ALC, BLC, AWB, DNR
4 | Power | 24v AC or POE/ AC 220V
5 | Video Output | IP Ethernet Protocol
6 | High shutter speed support | required
7 | Image Resolution | Min 2 Mega Pixel full HD
8 | IR Projector | Required(Car plate shall be read in 0.0Lux)
9 | Iris | Auto Iris
10 | Virtual PTZ | Yes
11 | Image Compression | M-JPEG , MPEG-4 , JPEG , H-264
12 | Direct activation with ground sensor (Loop detector) | Required
13 | photo taking | both Auto and Manual support
14 | Image processing | Embeded or ANPR (VTA)
15 | plate recognition @ Vehicle speed | Max 25 Km/h
16 | WDR | 120dB with turned on light of vehicle at day and night
17 | ground sensor (Loop detector) | Required
18 | Trafic light | Required (Red/Green)
19 | Barrier | Motorised -both Auto and Manual support
20 | RFID Tag Reader | Support
21 | Auto control for trafic light | Red/Green
22 | Auto control for road barrier | Required
23 | Data Bank for drivers and vehicles | Unlimited records and Support multiple reports
24 | Software Capabilities | multi binding for drivers and plates/ definition of mutiple groups and actions for different times and groups
25 | Min History Backup | 2 years
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 8 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## POLE
Pole |  |  | VENDOR REPLY
1 | Type | Standard, Octagonal continuously tapered
2 | Brand / Model Number | By Vendor
3 | Mounting Type | Flanged Mounted
4 | Material | ST37, Hot Dip Galvanized Steel
5 | Height(meter) | 8 meter for speed dome camera / 4 & 6 meter for fixed camera,
6 | Required Bolts and Nuts | Hot Deep Galvanized
7 | Options | Junction Box Bracket, Hole sleeve for cable entery and clamp type bracket
8 | Thickness(mm) | 8 meter hieght: 8 mm 6 meter hieght: 6 mm 4 meter hieght: 4 mm
9 | Plate and and brackets for installing cameras, Junction boxes, washer tanks and other accessories for cameras | Required
10 | Hole for cables (to JB and camera) | Required
11 | Plate Thickness And Other Details | As Per "Scope Of Work For Security System"
12 | Max Deflection At Max Wind | 10mm
13 | Lightning Protection | Required
14 | Number Of Arms | As Per Related Material Requisition Document
15 | Weight | By Vendor
16 | All the cabling such as power, data, earthing and lightening | Required
17 | Concrete / Concrete(Megr) | min 350 /150 kg/m3
18 | Foundation dimensions (L x W x H) | 8m: Min 150 x 150 x 150 cm 6m: Min 115 x 115 x 115 cm 4m: Min 85 x 85 x 90 cm
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 9 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## NVR
Network Video Recorder Server-Part 1 |  |  | VENDOR REPLY
1 | Number Of Ports | Joystick port, Additional USB port, 2 Gbps Fast Ethernet Port(1000Base-T)
2 | Brand / Model Number | By Vendor
3 | Labling | Required
4 | Mounting/ Mounting Accessories | Rack Mount/ Required
5 | Recording Storage Capacity | Required
6 | Hard Disk Drive Configuration | RAID 0,1,5,6
7 | Hard Type | Surveillance, Industrial 24*7,
8 | Model | HOT PLUG
9 | Hard Capacity Requirement | 2TB for per camera
10 | Software with license | Required
11 | Number of camera channels supports | Required
12 | Recording Rate | By Vendor
13 | Operating System | Required
14 | Processor | Xeon, 4GHz or higher
15 | Memory | Min. 2 GB DDR RAM
16 | Video Outputs | Required
17 | Optical Drive | Required
18 | Form Factor | Required
19 | Dimensions (LxWxH) | By Vendor
20 | Weight | By Vendor
21 | Operating Temperature | Required
22 | Rremote PC Client / Operating System | Required
23 | Features | Min. 30 fps speed for each camera and save for 30days with FUll HD quality 2TB HDD foor each camera
24 | Power Supply/ Power Consumption | 230VAC with minimum 600W redundant power supply
25 | Network Adapter (NIC) | Dual TCP/ IP Integrated 10/100/1000 Base –T
26 | Sound Card | In- Built
27 | Graphic Card | Super VGA non-interlaced graphics card capable of 1024x768 pixel resolution and 65K colors (or true color) with 4MB video memory or better
28 | Recording Speed | 30 fps/ channel (For all channel)-2 Mpixel
29 | Keyboards | PS2 Keyboard
30 | Mouse | Optical Mouse with scroll
31 | Operating system | MS Windows OS or Linux (Latest versions) at the time of tender
32 | Anti Virus Software | Latest software at the time of tender/ order
تسهیلات
DATA SHEET FOR CCTV
شماره صفحه: 10 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## NVR-2
Network Video Recorder Server-Part 2 |  |  | VENDOR REPLY
1 | Number Of Ports | CCTV Joystick port, Additional USB port, 2 Gbps Fast Ethernet Port(1000Base-T)
2 | Brand / Model Number | By Vendor
3 | Labling | Required
4 | Mounting/ Mounting Accessories | Rack Mount/ Required
5 | Recording Storage Capacity | Required
6 | Hard Disk Drive | By Vendor
7 | Analytic Software | Required
8 | Number of camera channels supports | By Vendor
9 | Recording Rate | Required
10 | Operating System | Required
11 | Processor | By Vendor
12 | Memory | By Vendor
13 | Video Outputs | Required
14 | Optical Drive | Required
15 | Form Factor | Required
16 | Dimensions (LxWxH) | By Vendor
17 | Operating Temperature | Required
18 | Rremote PC Client / Operating System | Required
19 | Features | Min. 25 fps speed for each camera and save for 30days with FUll HD quality 2TB HDD foor each camera
20 | Power Supply/ Power Consumption | 230VAC with minimum 600W redundant power supply
21 | Network Adapter (NIC) | Dual TCP/ IP Integrated 10/100/1000 Base –T
22 | Sound Card | In- Built
23 | Graphic Card | Super VGA non-interlaced graphics card capable of 1024x768 pixel resolution and 65K colors (or true color) with 4MB video memory or better
24 | Keyboards | USB Keyboard
25 | Mouse | Optical Mouse with scroll
26 | Operating system | MS Windows OS or Linux (Latest versions) at the time of tender
27 | Anti Virus Software | Latest software at the time of tender/ order
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 11 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Management Software
Video Management Software(VMS) |  |  | VENDOR REPLY
1 | Operating System | Windows Server 2003, 2008, 2012 Window XP, Vista, 7, 8, 10
2 | Network | Ethernet, 1 Gbit or higher recommended.
3 | Hardware Requirements | x86 Platform
4 | Server requirement (for 640x480 resolution) | Core i7 (6 Cores), 3 GHz, 8 GB for up to 18 channels Xeon 6 core, 3 GHz, 8 GB for up to 18 channels Xeon 12 core, 3 GHz, 16 GB for up to 36 channels (approx. 3 channels/core, suitable to add multiple CPUs per server) Supports Nvidia GPU acceleration for Face Capture & Recognition (approx. 1 channel/2 cores for Face Recognition based features) Note: For higher resolution and larger feature set consult AllGoVision
5 | Frame Rate Requirement | >8 fps for Security Analytics (Perimeter Protection/Intrusion), Face Recognition >15 fps for PTZ Analytics, People Counting, Traffic features and LPR.
6 | Camera Support | Supports MJPEG, H.264, MPEG4 Supports ONVIF camera, ONVIF PTZ control
7 | Video Analytics Software requirment | People Counting,Reporting & Analysis,Vehicle Counting,Wrong Way Detection,Speeding and Any change Detection,License Plate Detection,Face Detection / Face Capture,Face Recognition / Verification,Auto Tracking,Ramble Detection
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 12 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Video Wall (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Inustrial Video Wall |  |  | VENDOR REPLY
1 | Diagonal screen size (inch) | Minimum 46 Inch
2 | Panel resolution | 1920x1080p
3 | Size | maximum to 1212x685x102
4 | Optimum resolution | 1920 x 1080 @ 60 Hz
5 | Brightness | 450 cd/m²
6 | Contrast ratio (typical) | 1400:1
7 | Dynamic contrast ratio | 500,000:1
8 | Response time (typical) | 8 ms
9 | Aspect ratio | 16:09
10 | Display colors | 1073 M
11 | Video input | DVI-D,HDMI (x2),VGA (Analog D-Sub),DisplayPort (1.2),Component (BNC x3),Composite (BNC)
12 | Video output | DisplayPort,DVI-I,VGA (via DVI-I)
13 | MTBF(in Semi-light) | 100,000 hour(s)
14 | Bezel thickness | Maximum 1.8 mm(as per contract)
15 | Optional accessories | Edge finishing kit
ColourCalibrationKit
HDBaseT OPS Receiver
IR Light Motion Sensor
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 13 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Video Wall Controller (2)
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Video Wall Controller System
| Hardware |  | VENDOR REPLY
1 | CPU | Intel® i5 6-core 2.9GHz
2 | SSD | 1x 500GB SSD Optional: 2 x 500GB SSD RAID1
3 | Backplane | 4x Slot PCI Express x16
4 | Network | 1x 10GbE + 1x 1GbE
5 | Case | 19” 4RU case
6 | Power Supply | 230 VAC
7 | MTBF | 100,000hrs
Software
8 | OS | Windows, 64 Bit
9 | Recovery | Easy backup and recovery USB
10 | Max number of outputs | Up to 12x
11 | Configuration | High End NVIDIA Quadro GPU with 4x outputs per card / Max. 32,768x32,768 pixel per system
12 | Resolution | VS-2-4HO card: HDMI 2.0, 4x 4096x2160@60Hz per card VS-2-4DO card: DisplayPort 1.4, 4x 5120x3200@60Hz per card
13 | Desplayy Input Port 1.2 | Up to 6x
14 | HDMI 1.4 | Up to 12x
15 | SDI | 6x3G and 6x12G
16 | Stream Format | Protocols: RTSP, RTP, MPEG-2-TS, SRT; Distribution: unicast & multicast; Codec: H.264 (MPEG-4 Part 10 AVC) up to Level 5.2; Profiles: Baseline, Main, High, High 10, High 4:2:2, High 4:4:4 Predictive Profile Separate Plane
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 14 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## industrial desktop Monitor
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Industrial LED Monitor (Desktop Monitor) |  |  | VENDOR REPLY
1 | Display Resolution | Full HD (1920 × 1080 Pixel )
2 | Size | 22 inch to 25 inch
3 | Viewing Angle | H 160º / V 160º
4 | Display Technology | IPS
5 | MTBF | >30,000 h
6 | Response Time | <9 ms
7 | Aspect Ratio | 16:09
8 | Contrast Ratio | 1000:01
9 | Brightness | >=300 cd/m²
10 | Pixel Pitch | <0.4 mm
11 | Ambient Light Sensor | Automatic
12 | Input Voltage | 220 VAC
13 | Inputs | DVI , RGB(HD15),BNC(for analog cctv), SVIDEO, RJ45,HDMI
14 | Panel Life Time cycle | 24/7 ( 24 Hour in 7 Day in Week)
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 15 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Switch
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Industrial Outdoor Switch |  |  | VENDOR REPLY
1 | 10/100BASE (RJ-45 Connector) Ports | 4 or 8
2 | 1000BASE (SFP) Ports | Min 2
3 | GLC type | SM (single mode) and the single strand bidirectional
4 | Boud rate | 100/1000
5 | Body material | Metal
6 | POE Mode | HPOE Support-Ring Support
7 | Operation Temperature Range | According to Climate Data(Maximum 70 C)
8 | Network Layer | 2 Layers
9 | Config status | Secure Configable with Command Prompt
10 | Power | 220-230 VAC
11 | Other Featchres | Modular
Rack Mounted Netweork Switch
12 | 10/100/1000 BASE (RJ-45 Connector) Ports | 24 or 48
13 | 1000BASE (SFP) Ports | Minimum 12 SFP
14 | GLC type | SM (single mode) and the single strand bidirectional
15 | Boud rate | 100/1000
16 | Body material | Metal
17 | POE Mode | Support, also Ring Support
18 | Operation Temperature Range | 0° to 40° C
19 | Network Layer | 2 & 3
20 | Config status | Secure Configable with Command Prompt
21 | Power | 220-230 VAC
22 | Other Featchres | Modular and Rackmount
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 16 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Intercom-Rack
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Outdoor Intercom |  |  | VENDOR REPLY
1 | Certificate | Ul,EN,
2 | operating Temperature | up to 70C
3 | Humidity | minimum 95%
4 | capability to record | Yes
5 | Remote monitoring | Yes
6 | Direct Access and dynamic Keys & LEDs | Yes
7 | Alarm features | Pre Recordded Alarm Tones, Pre ecorded Speech Messages, Capability to Route Audio to Individually controlled Zones, Scheduled Events
8 | Nerwork Protocols | IPv4, SIP, TCP, UDP,HTTPS,TFTP, RTP,DHCP,SNMP,NTP
9 | ingress Protection | minimum IP66
10 | IK rating | minimum IK08
11 | corrosion-resistant,salty mist | Yes, According to EN60945
13 | UV-resistant | yes
14 | EMC | Yes, According to CE and FCC rules
15 | Active Noise reduction | yes
16 | adjustable microphone sensitivity and volume | yes
17 | Capability of working serverless | yes
CCTV Cabinet
18 | ingress Protection | IP 42
19 | Accessories | Fan, ligth , heater , earth bar , fuse ,Power Socket(8 Port)
20 | Door Lock | Required
21 | Ral | 7035
22 | Size | 19" ,Minimum 42 Unit
23 | Type | Movable with wheel
24 | Temprature Desplay | Required
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 17 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## Desktop Call Station
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
Desktop Call Station(With Neck swan mic) |  |  | VENDOR REPLY
1 | Type of Installation | Desk Mount
2 | Number of keys | >16
3 | Brand / Model Number | By Vendor
4 | Labling | By Vendor
5 | Material | By Vendor
6 | Protection index | Min. IP20
7 | Type of Installation | Desk Mount
8 | Power | 230 VAC, 50 Hz
9 | Site and Zone Selection | YES (One / Many / Pre-Defined Group / All)
10 | Noise-Canceling Microphone | Required
11 | Routine Speed Press-to-Talk Switch | Required
13 | Dual action "Emergency Speed" Push Button | Required
14 | Dual Action Latching Manual Alarm | Required
15 | Push Buttons (for each alarm type) | Required
16 | "Access Granted" Indicator | Required
17 | Broadcast Area-Selected Indicators | Required
18 | System 'Busy' or 'In Use' Indication | Required
19 | System 'Healthy' Indication | Required
20 | Selected and Playback of Pre-recorded Speech Message | Required
21 | Power Fail Indication | Required
22 | Local control station visual alarm | Required
23 | System monitoring equipment | Required
24 | Keyboard and Microphone | Required
25 | Control and zone selection circuitry | Required
26 | Number of keys | >16
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 18 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK

## CCTV Client Software
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
CCTV Client Harsware |  |  | VENDOR REPLY
1 | Operating System | Windows 10 Pro 64-bit
2 | CPU | Intel® Core i5, such as Intel® Core i5-8500
3 | RAM | 8GB, DDR4-2666 MHz
4 | Graphic card | Intel® HD Graphics 630
5 | Network | 1 Gbps
CCTV Client Software
7 | Control and view Minium 4 camera feeds simultaneously on 22 inch | Required
8 | Use IP cameras as well | Required
9 | Pan/Tilt/Zoom (PTZ) support for many network cameras | Required
10 | Digitally zoom, even if your camera does not support it | Required
11 | Adjust the orientation of live feeds | Required
12 | View cameras on Multiple Monitors | Required
13 | Capture JPEG, MJPEG, MPEG-4 and H.264 stream from IP cameras | Support
تسهیلات
TBE FOR CCTV SYSTEM
شماره صفحه: 19 از19
NISOC
شماره پیمان:
9184-073-053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
IN
DT
0020
D01
بسته کاری
GCS
پروژه
BK