## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-W007S-PEDCO-110-CV-PY-0003-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-1083 |  |  | Transmital Date: 15-Jun-2022
Document Title: General Civil Layout - Extension of Binak B/C Manifold |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0005-CV-TR-1083 |  |  | Transmital Date: 15-Jun-2022
[5 empty] | CRS No: NISOC-CRS-BK-W007S-PEDCO-110-CV-PY-0003-D00 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
A | بخش عمومی - رعایت کامل مفاد صورتجلسه‌ی نامه شماره 443041 مورخ 1400/12/18 مدنظر قرار گیرد. |  | 01/2294/113987 | 1401/04/03 | مفاد صورتجلسه در زیر ارائه و پاسخ داده شده است.
A-1 | مقرر گردید توسعه فنس کلاستر از سمت جاده مجاور به گونه ای باشد که عرض باقی مانده از جاده حداقل 5 متر بماند. |  | صورتجلسه‌ی نامه شماره 443041 | 1400/12/18 | عرض جاده پاترول جدید 5 متر می‌باشد.
A-2 | مقرر گردید خط کنارگذر لوله 10 اینچ فلر به منظور ایجاد فضای توسعه ای به صورت عمودی اصلاح گردد. |  | صورتجلسه‌ی نامه شماره 443041 | 1400/12/18 | اقدامات مقتضی صورت می‌گیرد.
A-3 | مقرر گردید فضای بین فنس و آخرین لوله به میزان 60 سانتی متر فضای دسترسی در نظر گرفته شود. (رجوع به جزئیات A) |  | صورتجلسه‌ی نامه شماره 443041 | 1400/12/18 | اصلاح گردید.
A-4 | مقرر گردید از انتهای فنس موجود کارخانه، دیوار چینی به ارتفاع حدقل یک متر به نحوی اجرا شود که حداقل از نظر ارتفاعی به میزان 20 سانتی متر بالاتر از لوله های خروجی از فنس قرار گیرد. (رجوع به جزئیات C) |  | صورتجلسه‌ی نامه شماره 443041 | 1400/12/18 | اصلاح گردید و دیوار با عرض 40 سانتی متر و ارتفاع 1 متر اجرا می‌گردد.
A-5 | استفاده از سنگ، توری فنس، متریال آهن، سیم خاردار موجود برای توسعه فنس جدید توسط پیمانکار پروژه بلامانع است. |  | صورتجلسه‌ی نامه شماره 443041 | 1400/12/18 | اقدامات مقتضی صورت می‌گیرد.
B | بخش مهندسی مکانیک - پیرو بررسی بعمل آمده، به نحوه‌ی نصب و فونداسیون پمپ Sump در طرح ارسالی هیچ اشاره‌ای نشده است. اقدام شود. |  | 01/2294/113987 | 1401/04/03 | اعمال شد.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By: | Signature
| Date: |  |  |  |  | Date: