## Cover
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR EXPANSION OF MV SWITCHGEAR
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 10
9184 – 073 - 053 |  |  | BK |  | GCS | PEDCO | 120 |  | EL | DT | 0004 | D02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS FOR EXPANSION OF MV SWITCHGEAR نگهداشت و افزایش تولید میدان نفتی بینک
D02 |  | Jul.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D01 |  | Mar.2022 |  | IFA |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
D00 |  | Dec.2021 |  | IFC |  |  |  | H.Shakiba |  |  | M.Fakharian |  | M.Mehrshad
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
Class: 2 |  |  |  | CLIENT Doc. Number: F0Z-709021
status: | IDC: Inter-Discipline Check
IFC: Issued For Comment
IFA: Issued For Approval
AFD: Approved For Design
AFC: Approved For Construction
AFP: Approved For Purchase
AFQ: Approved For Quotation
IFI: Issued For Information
AB-R: As-Built for CLIENT Review
AB-A: As-Built –Approved

## REVISION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح‌الارض احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
DATA SHEET FOR EXPANSION OF MV SWITCHGEAR
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 10
9184 – 073 - 053 |  |  | BK | GCS |  | PEDCO | 120 | EL | DT | 0004 |  | D02
REVISION RECORD SHEET
Page | D00 | D01 | D02 |  | D03 |  | D04 |  | Page |  | D00 |  | D01 |  | D02 | D03 | D04
1 | X | X | X | [5 empty] | 51
2 | X | X | X | [5 empty] | 52
3 | X | X | X | [5 empty] | 53
4 | X | X | X | [5 empty] | 54
5 | X | X | X | [5 empty] | 55
6 | X | X | X | [5 empty] | 56
7 | X | X | X | [5 empty] | 57
8 | X | X | X | [5 empty] | 58
9 |  | X | X | [5 empty] | 59
10 |  | X | X | [5 empty] | 60
11 | [8 empty] | 61
12 | [8 empty] | 62
13 | [8 empty] | 63
14 | [8 empty] | 64
15 | [8 empty] | 65
16 | [8 empty] | 66
17 | [8 empty] | 67
18 | [8 empty] | 68
19 | [8 empty] | 69
20 | [8 empty] | 70
21 | [8 empty] | 71
22 | [8 empty] | 72
23 | [8 empty] | 73
24 | [8 empty] | 74
25 | [8 empty] | 75
26 | [8 empty] | 76
27 | [8 empty] | 77
28 | [8 empty] | 78
29 | [8 empty] | 79
30 | [8 empty] | 80
31 | [8 empty] | 81
32 | [8 empty] | 82
33 | [8 empty] | 83
34 | [8 empty] | 84
35 | [8 empty] | 85
36 | [8 empty] | 86
37 | [8 empty] | 87
38 | [8 empty] | 88
39 | [8 empty] | 89
40 | [8 empty] | 90
41 | [8 empty] | 91
42 | [8 empty] | 92
43 | [8 empty] | 93
44 | [8 empty] | 94
45 | [8 empty] | 95
46 | [8 empty] | 96
47 | [8 empty] | 97
48 | [8 empty] | 98
49 | [8 empty] | 99
50 | [8 empty] | 100

## 11 KV
Technical Data For Expansion of 11 KV MV Switchgear
Rev | Item | Description | Required | Vendor Data
Environmental Data
D00 | 1.1 | Name of Project / Plant | Binak Oilfield in Bushehr Province
D02 | 1.2 | Ambient Temperature (Min/Max) | Min ~ Max: +5 ~ +52°C
D00 | 1.3 | Max.Design Temperature: | 50 °c
D00 | 1.4 | Max. Sun Temperature: | + 85 °c
D00 | 1.5 | Max.Relative Humidity: | 100%
D00 | 1.6 | Mean Sea Level: | 12.5 m Above Sea Level
D00 | 1.7 | Seismic Factor: | 0.3g
D00 | 1.8 | Max. Wind Velocity(Max) | 120 km/hr
2-Switchgear
D00 | 2.1 | Manufacturer | By Vendor
D00 | 2.2 | Standard(s) | IPS-M-EL-144(4), IPS-E-EL-100(1), BK-GNRAL-PEDCO-000-EL-SP-0005
D00 | 2.3 | Quantity | 8 Feeders of Ougoing, Type C2 & C3
D00 | 2.4 | Service | Expansion of Exsiting MV Switchgear from Both Side
D00 | 2.5 | Tag Number | GCS-11-SWG-001A/B
D00 | 2.6 | Applicable SLD | BK-GCS-PEDCO-120-EL-SL-0001 BK-GCS-PEDCO-120-EL-SL-0003 BK-GCS-PEDCO-120-EL-DG-0001
D00 | 2.7 | Location | Indoor
D00 | 2.8 | Type and Construction | Metal Clad, Withdrawable
D01 | 2.9 | Rated Voltage & Variation | 11 kV ± 10 %
D00 | 2.10 | Rated Frequency & Variation | 50 Hz ± 5 %
D00 | 2.11 | No. of Phases | 3 PH
D02 | 2.12 | Rated Insulation Levels between earth and phase • One Minute Power Frequency Withstand Voltage (RMS) • One Minute Power Frequency Withstand Voltage of Aux. Circuit (RMS) • Impulse Withstand Voltage (Peak) | 28 KV 75 KV 2 KV
D00 | 2.13 | Rated Normal Current of Busbars | 1600 A
D01 | 2.14 | Rated Short Time Current of Busbar | 25 kA; 1 sec (Note 9.2)
D00 | 2.15 | Rated Peak Withstand Current | 63 kA
D01 | 2.16 | Busbars: • Material • Main Horizontal Bus Cross Section Area • Main Vertical Bus Cross Sectional Area • Earth Bus Cross Sectional Area • Busbars Color & Joints | Copper (Flame Retardant Non-Hygroscopic) Vendor to Advise Vendor to Advise Vendor to Advise Silver Plated
D00 | 2.17 | Maximum Tolerable Temperature Rise | Acc. to IEC62271 IPS-M-EL-144(4)
D00 | 2.18 | Rated Voltage for Control And Protection Circuits | 110 V DC
D00 | 2.19 | Rated Voltage for Space Heaters and Panel Lighting | 400 / 230 VAC
D00 | 2.20 | Enclosure | Withdrawable Metal Clad, Compartmented
D01 | 2.21 | Degree of Protection by Enclosure | External: IP 42, Internal: IP 20, Internal partitions between functional units and shutters for bus bar & cable side: IP 4X
D00 | 2.22 | Installation | Floor Self-Standing, Side by Side
D00 | 2.23 | Rear / Front Access | Rear and Front Access
D00 | 2.24 | Top / Bottom Cable Entry | Cables: Bottom Entry
D00 | 2.25 | Sheet Steel Thickness, Fram & Walls | Minimum 2.5 mm
D00 | 2.26 | Paint | Electrostatic Powder
D00 | 2.27 | Color finish | RAL 7032
D00 | 2.28 | Routine Tests | Required (Withstand tests and reports as per IEC 62271-200 or IEC 298, IEC 60694, IPS-M-EL-144 (4) and Specification)
D00 | 2.29 | Type Tests | Test certificates of the SWGR type as per IEC62271-200 or IEC 298, IEC60694, and IPS-M-EL-144 (4)
D00 | 2.30 | Overall Dimensions (HxWxD) [mm] | Vendor to Advise
D00 | 2.31 | Total Weight [kg] | Vendor to Advise
D00 | 2.32 | Overall Dimensions of 1 Cubicle (HxWxD) | Vendor to Advise
D00 | 2.33 | Dynamic Load of One Cubicle [kg] | Vendor to Advise
3.MV Circuit Breaker
D00 | 3.1 | Manufacturer | Vendor to Advise
D00 | 3.2 | Standard | IEC62271-100
D00 | 3.3 | Type | Vacuum
D00 | 3.4 | Fixed/ Withdrawable | Withdrawable
D02 | 3.5 | Rated Voltage | 12 kV ± 10 %
D00 | 3.6 | Rated Frequency | 50 Hz ± 5 %
D00 | 3.7 | No. Of Phases and Poles | 3-Phase
D00 | 3.8 | Rated Insulation Levels between earth and phase • One Minute Power Frequency Withstand Voltage (RMS) • One Minute Power Frequency Withstand Voltage of Aux. Circuit (RMS) • Impulse Withstand Voltage (Peak) | 28 KV 2 KV 75 KV
D00 | 3.9 | Rated Normal Current | 630 A
D00 | 3.10 | Rated Short Time Current | 25 kA
D00 | 3.11 | Rated Peak Withstand Current | 62.5 kA
D00 | 3.12 | Rated Short Circuit Breaking Current | Vendor to Advise
D00 | 3.13 | Rated Short Circuit Making Current | Vendor to Advise
D00 | 3.14 | Maximum Tolerable Temperature Rise | Acc. to IEC62271-100
D00 | 3.15 | Design Temperature Rise | Acc. to IEC62271-100
D00 | 3.16 | Operating Mechanism | Motor & Hand operated Spring Charged Stored Energy Mechanism
D00 | 3.17 | Release type | Shunt Trip
D00 | 3.18 | Rated Operating Sequence | O-0.3S-CO-3MIN-CO
D00 | 3.19 | Rated Voltage of Auxiliary Equipment | 110V DC
D00 | 3.20 | Rated Operating Voltage of Releases | 110V DC
D00 | 3.21 | Rated Operating Voltage of Charging Motors | 110V DC
D00 | 3.22 | Voltage Tolerances for Auxiliary Apparatus: • Trip Circuit • Close Circuit • Motor Running • Motor at the Instant of Start | 70%-110% 85%-110% 85%-110% 70%-110%
D00 | 3.23 | Power consumption of Auxiliary Apparatus:[W] • Trip Circuit • Closed Circuit • Charging motor • Under voltage release • Multifunction relay • Transducers | 110V DC Vendor to Advise
D00 | 3.24 | 1 C.B. Open/Close Auxiliary Contacts: • No. Of Make Contacts • No. Of Break Contacts • Rated Voltage • Rated Current at 110V DC • Breaking Current at 110V DC | 6 6 110V DC VTA VTA
D00 | 3.25 | Truck Position Auxiliary Contacts: • No of Make Contacts • No of Break Contacts • Rated Voltage • Rated Current at 110V DC • Breaking Current at 110V DC | 1NO + 1NC 1NO + 1NC 110V DC VTA VTA
D00 | 3.26 | Routine Tests | IEC62271-100
D00 | 3.27 | Type Tests | IEC62271-100
4.MV Voltage Transformers
D00 | 4.1 | Manufacturers Name | Vendor to Advise
D00 | 4.2 | Standard | IEC60044-2
D00 | 4.3 | Type | Epoxy Cast Resin
D00 | 4.4 | Fixed Withdrawable | Withdrawable
D00 | 4.5 | Highest System Voltage | 12 kV
D00 | 4.6 | Rated Frequency | 50 Hz
D00 | 4.7 | No. of Phase | Single Phase
D00 | 4.8 | Rated Primary Voltage [kV] | 11/√3 kV
D00 | 4.9 | Rated Secondary Voltage [V] | 110/√3 V
D00 | 4.10 | Rated Insulation Levels between earth and phase • One Minute Power Frequency Withstand Voltage (RMS) • One Minute Power Frequency Withstand Voltage of Aux. Circuit (RMS) • Impulse Withstand Voltage (Peak) | 28 kV / √3 2 kV / √3 75 kV / √3
D00 | 4.11 | System Earthing | TNS
D00 | 4.12 | Rated Voltage Factor | Vendor to Advise
D00 | 4.13 | Rated Burden | Vendor to Advise
D00 | 4.14 | Accuracy Class: • for Protection (with separate Winding) • for Measuring (with separate Winding) | CL. 3P 1.0
D00 | 4.15 | Insulation Class & Temperature Rise | Class E, Temp. Rise Class Y
5.MV Current Transformers
D00 | 5.1 | Manufacturer’s Name | Vendor to Advise
D00 | 5.2 | Standard | IEC60044-1
D00 | 5.3 | Type | Dry Type
D00 | 5.4 | Highest System Voltage | 11 kV
D00 | 5.5 | Rated Frequency | 50 Hz
D00 | 5.6 | Rated Secondary Current: | 1 A / 5 A According to SLD
D00 | 5.7 | Rated Continuous Thermal Current: | 1.2 x Rated primary current
D00 | 5.8 | Rated Short Time, Current: | 25 kA, 1 Sec
D00 | 5.9 | Rated Dynamic Current: | 63 kA
D00 | 5.10 | Rated Burden | Vendor to Advise
D00 | 5.11 | Rated Transformation Ratio and No. of Cores | According to Single Line Diagram
D00 | 5.12 | Accuracy Class: • Measuring • Protection | Class 1: Class 1FS5 Class X: where required Class 5P20 protections
D00 | 5.13 | Routine Tests | IEC60044-1
D00 | 5.14 | Type Tests | IEC60044-1
D01 | 5.15 | Rated Insulation Levels between earth and phase • One Minute Power Frequency Withstand Voltage (RMS) • One Minute Power Frequency Withstand Voltage of Aux. Circuit (RMS) • Impulse Withstand Voltage (Peak) | 28 kV / √3 2 kV / √3 75 kV / √3
6.Earth Switch
D00 | 6.1 | Manufacturer’s Name | Vendor to Advise
D00 | 6.2 | Manufacturer’s Type Designation | Vendor to Advise
D00 | 6.3 | Standard | IEC62271-102
D00 | 6.4 | Type | Make Proof
D00 | 6.5 | Number Of Phase | 3
D00 | 6.6 | Frequency | 50 Hz
D00 | 6.7 | Rated Voltage | 11 kV
D00 | 6.8 | Rated Lighting Impulse Withstand Voltage | 75 kV
D00 | 6.9 | Rated 1 Minute Power Frequency Voltage | 28 kV
D00 | 6.10 | Rated Short Time (1s) Current | 25 kA
D00 | 6.11 | Rated Peak Withstand Current | 62.5 kA
D00 | 6.12 | Rated Short Circuit Making Current | 62.5 kA
D00 | 6.13 | Actuation Mechanism | Pre-tension Spring
D00 | 6.14 | No. of Auxiliary Contacts (Min.) | 2NO + 2NC
D00 | 6.15 | Aux. Contacts Rated Voltage | 110V DC
D00 | 6.16 | Aux. Contacts Rated Current | 1A
D00 | 6.17 | Interlocks | According (but not limited) to Appendix B of IPS-M-EL-144 (4) specifically: To prevent closure of Earth Switch when CB is not in Test or withdraw position To prevent Insertion of CB when Earth Switch is connected. To prevent connection of Earth Switch when upstream Switch is not open i.e. electromagnetic coil (only for incoming)
D00 | 6.18 | Routine Tests | IEC62271-102
D00 | 6.19 | Type Tests (Certificates) | IEC62271-102
7.Motor Feeder Protection Relay
D00 | 7.1 | Manufacturer’s Name | Vendor to Advise
D00 | 7.2 | Manufacturer’s Type Designation | Vendor to Advise
D00 | 7.3 | Type | Digital Multi-Function Relay + Display with adjustment Menu
D00 | 7.4 | Installation | Flush Mounted
D02 | 7.5 | Included Protection (ANSI Codes) | 50, 51, 46, 51LR, 49, 66, 50G, 51G, 26, 87M, 86 (Separate Relay)
D00 | 7.6 | Rated Current [A] | 5
D00 | 7.7 | Rated Frequency [Hz] | 50 Hz
D00 | 7.8 | Burden [VA] | Vendor to Advise
D00 | 7.9 | Overload Capability Of Current Path | 100xIn < 1 Sec.
D00 | 7.10 | Rated Voltage Auxiliary Voltage [V] | 110V DC
D00 | 7.11 | Auxiliary Voltage Permissible Range [V] | Min. ± 15% of Un
D00 | 7.12 | Power Consumption [W] | Vendor to Advise
D00 | 7.13 | Trip Relay Contacts | 2NO + 2NC at least
D00 | 7.14 | Alarm Relay Contacts | 2NO + 2NC at least
D00 | 7.15 | Auxiliary Contacts Ratings • Contacts Voltage Rating [V] • Contacts Rated Continuous Current | 110V DC Vendor to Advise
D00 | 7.16 | Ingress Protection | IP42
D00 | 7.17 | Routine Tests | IEC 255
D00 | 7.18 | Type Tests (Certificates) | IEC 255
8. Transformer Feeder Protection Relay
D01 | 8.1 | Manufacturer’s Name | Vendor to Advise
D01 | 8.2 | Manufacturer’s Type Designation | Vendor to Advise
D01 | 8.3 | Type | Digital Multi-Function Relay + Display with adjustment Menu
D01 | 8.4 | Installation | Flush Mounted
D01 | 8.5 | Included Protection (ANSI Codes) | 50, 51, 51N,50G (Separate Relay)
D01 | 8.6 | Rated Current [A] | 5
D01 | 8.7 | Rated Frequency [Hz] | 50 Hz
D01 | 8.8 | Burden [VA] | Vendor to Advise
D01 | 8.9 | Overload Capability Of Current Path | 100xIn < 1 Sec.
D01 | 8.10 | Rated Voltage Auxiliary Voltage [V] | 110V DC
D01 | 8.11 | Auxiliary Voltage Permissible Range [V] | Min. ± 15% of Un
D01 | 8.12 | Power Consumption [W] | Vendor to Advise
D01 | 8.13 | Trip Relay Contacts | 2NO + 2NC at least
D01 | 8.14 | Alarm Relay Contacts | 2NO + 2NC at least
D01 | 8.15 | Auxiliary Contacts Ratings • Contacts Voltage Rating [V] • Contacts Rated Continuous Current | 110V DC Vendor to Advise
D01 | 8.16 | Ingress Protection | IP42
D01 | 8.17 | Routine Tests | IEC 255
D01 | 8.18 | Type Tests (Certificates) | IEC 255
9.Notes
D00 | 9.1 | According to "BK-GCS-PEDCO-120-EL-SL-0003", in the extension of existing MV switchgear, there are only 8 outgoing feeder for 11 KV switchgear & no extension is required for incoming & outgoing.
D01 | 9.2 | The rated short time current of busbar & rated peak withstand current will be recheked after power system study.
D01 | 9.3 | Minimum conductor sizes shall be 2.5 mm2 for protection (CT/PT) and bonding conductors and 1.5 mm2 for control and signal wiring.
D01 | 9.4 | Accessories required for proper and safe operation of the switchgear shall be supplied by vendor
تسهیلات
DATA SHEET FOR EXPANSION OF MV SWITCHGEAR
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
DT
0004
D02
بسته کاری
GCS
پروژه
BK

## 3.3 KV
Technical Data for Starter Panel of Fire Water Pump
Rev | Item | Description | Required | Vendor Data
Environmental Data
D00 | 1.1 | Name of Project / Plant | Binak Oilfield in Bushehr Province
D02 | 1.2 | Ambient Temperature (Min/Max) | Min ~ Max: +5 ~ +52°C
D00 | 1.3 | Max.Design Temperature: | 50 °c
D00 | 1.4 | Max. Sun Temperature: | + 85 °c
D00 | 1.5 | Max.Relative Humidity: | 100%
D00 | 1.6 | Mean Sea Level: | 12.5 m Above Sea Level
D00 | 1.7 | Seismic Factor: | 0.3g
D00 | 1.8 | Max. Wind Velocity(Max) | 120 km/hr
2-Switchgear
D00 | 2.1 | Manufacturer | By Vendor
D00 | 2.2 | Standard(s) | IPS-M-EL-144(4), IPS-E-EL-100(1), BK-GNRAL-PEDCO-000-EL-SP-0005
D00 | 2.3 | Quantity | 1 Feeder of Outgoing, Type C3
D00 | 2.4 | Service | Expansion of Exsiting MV Switchgear from Both Side
D00 | 2.5 | Tag Number | GCS-3.3-SWG-001
D00 | 2.6 | Applicable SLD | BK-GCS-PEDCO-120-EL-SL-0001 BK-GCS-PEDCO-120-EL-SL-0003 BK-GCS-PEDCO-120-EL-DG-0001
D00 | 2.7 | Location | Indoor
D00 | 2.8 | Type and Construction | Metal Clad, Withdrawable
D01 | 2.9 | Rated Voltage & Variation | 3.6 kV ± 10 %
D00 | 2.10 | Rated Frequency & Variation | 50 Hz ± 5 %
D00 | 2.11 | No. of Phases | 3 PH
D02 | 2.12 | Rated Insulation Levels between earth and phase • One Minute Power Frequency Withstand Voltage (RMS) • One Minute Power Frequency Withstand Voltage of Aux. Circuit (RMS) • Impulse Withstand Voltage (Peak) | 10 KV 40 KV 2 KV
D00 | 2.13 | Rated Normal Current of Busbars | 630 A
D01 | 2.14 | Rated Short Time Current of Busbar | 25 kA; 1 sec (Note 8.2)
D00 | 2.15 | Rated Peak Withstand Current | 63 kA
D01 | 2.16 | Busbars: • Material • Main Horizontal Bus Cross Section Area • Main Vertical Bus Cross Sectional Area • Earth Bus Cross Sectional Area • Busbars Color & Joints | Copper (Flame Retardant Non-Hygroscopic) Vendor to Advise Vendor to Advise Vendor to Advise Silver Plated
D00 | 2.17 | Maximum Tolerable Temperature Rise | Acc. to IEC62271 IPS-M-EL-144(4)
D00 | 2.18 | Rated Voltage for Control And Protection Circuits | 110 V DC
D00 | 2.19 | Rated Voltage for Space Heaters and Panel Lighting | 400 / 230 VAC
D00 | 2.20 | Enclosure | Withdrawable Metal Clad, Compartmented
D01 | 2.21 | Degree of Protection by Enclosure | External: IP 42, Internal: IP 20, Internal partitions between functional units and shutters for bus bar & cable side: IP 4X
D00 | 2.22 | Installation | Floor Self-Standing, Side by Side
D00 | 2.23 | Rear / Front Access | Rear and Front Access
D00 | 2.24 | Top / Bottom Cable Entry | Cables: Bottom Entry
D00 | 2.25 | Sheet Steel Thickness, Fram & Walls | Minimum 2.5 mm
D00 | 2.26 | Paint | Electrostatic Powder
D00 | 2.27 | Color finish | RAL 7032
D00 | 2.28 | Routine Tests | Required (Withstand tests and reports as per IEC 62271-200 or IEC 298, IEC 60694, IPS-M-EL-144 (4) and Specification)
D00 | 2.29 | Type Tests | Test certificates of the SWGR type as per IEC62271-200 or IEC 298, IEC60694, and IPS-M-EL-144 (4)
D00 | 2.30 | Overall Dimensions (HxWxD) [mm] | Vendor to Advise
D00 | 2.31 | Total Weight [kg] | Vendor to Advise
D00 | 2.32 | Overall Dimensions of 1 Cubicle (HxWxD) | Vendor to Advise
D00 | 2.33 | Dynamic Load of One Cubicle [kg] | Vendor to Advise
3.MV Circuit Breaker
D00 | 3.1 | Manufacturer | Vendor to Advise
D00 | 3.2 | Standard | IEC62271-100
D00 | 3.3 | Type | Vacuum
D00 | 3.4 | Fixed/ Withdrawable | Withdrawable
D00 | 3.5 | Rated Voltage | 3.3 kV ± 10 %
D00 | 3.6 | Rated Frequency | 50 Hz ± 5 %
D00 | 3.7 | No. Of Phases and Poles | 3-Phase
D00 | 3.8 | Rated Insulation Levels between earth and phase • One Minute Power Frequency Withstand Voltage (RMS) • One Minute Power Frequency Withstand Voltage of Aux. Circuit (RMS) • Impulse Withstand Voltage (Peak) | 10 KV 2 KV 40 KV
D00 | 3.9 | Rated Normal Current | 630 A
D00 | 3.10 | Rated Short Time Current | 10 kA
D00 | 3.11 | Rated Peak Withstand Current | 62.5 kA
D00 | 3.12 | Rated Short Circuit Breaking Current | Vendor to Advise
D00 | 3.13 | Rated Short Circuit Making Current | Vendor to Advise
D00 | 3.14 | Maximum Tolerable Temperature Rise | Acc. to IEC62271-100
D00 | 3.15 | Design Temperature Rise | Acc. to IEC62271-100
D00 | 3.16 | Operating Mechanism | Motor & Hand operated Spring Charged Stored Energy Mechanism
D00 | 3.17 | Release type | Shunt Trip
D00 | 3.18 | Rated Operating Sequence | O-0.3S-CO-3MIN-CO
D00 | 3.19 | Rated Voltage of Auxiliary Equipment | 110V DC
D00 | 3.20 | Rated Operating Voltage of Releases | 110V DC
D00 | 3.21 | Rated Operating Voltage of Charging Motors | 110V DC
D00 | 3.22 | Voltage Tolerances for Auxiliary Apparatus: • Trip Circuit • Close Circuit • Motor Running • Motor at the Instant of Start | 70%-110% 85%-110% 85%-110% 70%-110%
D00 | 3.23 | Power consumption of Auxiliary Apparatus:[W] • Trip Circuit • Closed Circuit • Charging motor • Under voltage release • Multifunction relay • Transducers | 110V DC Vendor to Advise
D00 | 3.24 | 1 C.B. Open/Close Auxiliary Contacts: • No. Of Make Contacts • No. Of Break Contacts • Rated Voltage • Rated Current at 110V DC • Breaking Current at 110V DC | 6 6 110V DC VTA VTA
D00 | 3.25 | Truck Position Auxiliary Contacts: • No of Make Contacts • No of Break Contacts • Rated Voltage • Rated Current at 110V DC • Breaking Current at 110V DC | 1NO + 1NC 1NO + 1NC 110V DC VTA VTA
D00 | 3.26 | Routine Tests | IEC62271-100
D00 | 3.27 | Type Tests | IEC62271-100
4.MV Voltage Transformers
D00 | 4.1 | Manufacturers Name | Vendor to Advise
D00 | 4.2 | Standard | IEC60044-2
D00 | 4.3 | Type | Epoxy Cast Resin
D00 | 4.4 | Fixed Withdrawable | Withdrawable
D00 | 4.5 | Highest System Voltage | 3.6 kV
D00 | 4.6 | Rated Frequency | 50 Hz
D00 | 4.7 | No. of Phase | Single Phase
D00 | 4.8 | Rated Primary Voltage [kV] | 3.3/√3 kV
D00 | 4.9 | Rated Secondary Voltage [V] | 110/√3 V
D00 | 4.10 | Rated Insulation Levels between earth and phase • One Minute Power Frequency Withstand Voltage (RMS) • One Minute Power Frequency Withstand Voltage of Aux. Circuit (RMS) • Impulse Withstand Voltage (Peak) | 10 kV / √3 2 kV / √3 40 kV / √3
D01 | 4.11 | System Earthing | TNS by Resistor
D00 | 4.12 | Rated Voltage Factor | Vendor to Advise
D00 | 4.13 | Rated Burden | Vendor to Advise
D00 | 4.14 | Accuracy Class: • for Protection (with separate Winding) • for Measuring (with separate Winding) | CL. 3P 1.0
D00 | 4.15 | Insulation Class & Temperature Rise | Class E, Temp. Rise Class Y
5.MV Current Transformers
D00 | 5.1 | Manufacturer’s Name | Vendor to Advise
D00 | 5.2 | Standard | IEC60044-1
D00 | 5.3 | Type | Dry Type
D00 | 5.4 | Highest System Voltage | 3.6 kV
D00 | 5.5 | Rated Frequency | 50 Hz
D00 | 5.6 | Rated Secondary Current: | 1 A / 5 A According to SLD
D00 | 5.7 | Rated Continuous Thermal Current: | 1.2 x Rated primary current
D00 | 5.8 | Rated Short Time, Current: | 10 kA, 1 Sec
D00 | 5.9 | Rated Dynamic Current: | 63 kA
D00 | 5.10 | Rated Burden | Vendor to Advise
D00 | 5.11 | Rated Transformation Ratio and No. of Cores | According to Single Line Diagram
D00 | 5.12 | Accuracy Class: • Measuring • Protection | Class 1: Class 1FS5 Class X: where required Class 5P20 protections
D00 | 5.13 | Routine Tests | IEC60044-1
D00 | 5.14 | Type Tests | IEC60044-1
D01 | 5.15 | Rated Insulation Levels between earth and phase • One Minute Power Frequency Withstand Voltage (RMS) • One Minute Power Frequency Withstand Voltage of Aux. Circuit (RMS) • Impulse Withstand Voltage (Peak) | 10 kV / √3 2 kV / √3 40 kV / √3
6.Earth Switch
D00 | 6.1 | Manufacturer’s Name | Vendor to Advise
D00 | 6.2 | Manufacturer’s Type Designation | Vendor to Advise
D00 | 6.3 | Standard | IEC62271-102
D00 | 6.4 | Type | Make Proof
D00 | 6.5 | Number Of Phase | 3
D00 | 6.6 | Frequency | 50 Hz
D00 | 6.7 | Rated Voltage | 3.3 kV
D00 | 6.8 | Rated Lighting Impulse Withstand Voltage | 40 kV
D00 | 6.9 | Rated 1 Minute Power Frequency Voltage | 10 kV
D00 | 6.10 | Rated Short Time (1s) Current | 10 kA
D00 | 6.11 | Rated Peak Withstand Current | 62.5 kA
D00 | 6.12 | Rated Short Circuit Making Current | 62.5 kA
D00 | 6.13 | Actuation Mechanism | Pre-tension Spring
D00 | 6.14 | No. of Auxiliary Contacts (Min.) | 2NO + 2NC
D00 | 6.15 | Aux. Contacts Rated Voltage | 110V DC
D00 | 6.16 | Aux. Contacts Rated Current | 1A
D00 | 6.17 | Interlocks | According (but not limited) to Appendix B of IPS-M-EL-144 (4) specifically: To prevent closure of Earth Switch when CB is not in Test or withdraw position To prevent Insertion of CB when Earth Switch is connected. To prevent connection of Earth Switch when upstream Switch is not open i.e. electromagnetic coil (only for incoming)
D00 | 6.18 | Routine Tests | IEC62271-102
D00 | 6.19 | Type Tests (Certificates) | IEC62271-102
7.Motor Feeder Protection Relay
D00 | 7.1 | Manufacturer’s Name | Vendor to Advise
D00 | 7.2 | Manufacturer’s Type Designation | Vendor to Advise
D00 | 7.3 | Type | Digital Multi-Function Relay + Display with adjustment Menu
D00 | 7.4 | Installation | Flush Mounted
D00 | 7.5 | Included Protection (ANSI Codes) | 50, 51, , 50G, 51G, , 86 (Separate Relay)
D00 | 7.6 | Rated Current [A] | 5
D00 | 7.7 | Rated Frequency [Hz] | 50 Hz
D00 | 7.8 | Burden [VA] | Vendor to Advise
D00 | 7.9 | Overload Capability Of Current Path | 100xIn < 1 Sec.
D00 | 7.10 | Rated Voltage Auxiliary Voltage [V] | 110V DC
D00 | 7.11 | Auxiliary Voltage Permissible Range [V] | Min. ± 15% of Un
D00 | 7.12 | Power Consumption [W] | Vendor to Advise
D00 | 7.13 | Trip Relay Contacts | 2NO + 2NC at least
D00 | 7.14 | Alarm Relay Contacts | 2NO + 2NC at least
D00 | 7.15 | Auxiliary Contacts Ratings • Contacts Voltage Rating [V] • Contacts Rated Continuous Current | 110V DC Vendor to Advise
D00 | 7.16 | Ingress Protection | IP42
D00 | 7.17 | Routine Tests | IEC 255
D00 | 7.18 | Type Tests (Certificates) | IEC 255
8.Notes
D00 | 8.1 | According to "BK-GCS-PEDCO-120-EL-SL-0003", in the extension of existing MV switchgear, there is only 1 outgoing feeder for 3.3 KV switchgear & no extension is required for incoming & outgoing.
D01 | 8.2 | The rated short time current of busbar & rated peak withstand current will be recheked after power system study.
D01 | 8.3 | Minimum conductor sizes shall be 2.5 mm2 for protection (CT/PT) and bonding conductors and 1.5 mm2 for control and signal wiring.
D01 | 8.4 | Accessories required for proper and safe operation of the switchgear shall be supplied by vendor
تسهیلات
DATA SHEET FOR EXPANSION OF MV SWITCHGEAR
NISOC
شماره پیمان:
9184 – 073 - 053
نگهداشت و افزایش تولید میدان نفتی بینک
سطح‌الارض
احداث رديف تراكم گاز در ايستگاه جمع آوري بينك
صادرکننده
رشته
نوع مدرک
سریال
نسخه
PEDCO
120
EL
DT
0004
D02
بسته کاری
GCS
پروژه
BK