## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-PEDCO-120-EL-DT-0004-D01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-T-0705 |  |  | Transmital Date: 09-Mar-2022
Document Title: Data Sheets For Expansion of MV Switchgear |  |  |  |  | PEDCO Tr. No.: BK-PEDCO-NISOC-0012-EL-TR-0705 |  |  | Transmital Date: 09-Mar-2022
[5 empty] | CRS No: NISOC-CRS-BK-GCS-PEDCO-120-EL-DT-0004-D01 |  |  | CRS Status:
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | جهت فیدر تغذیه موتوری مربوط به الکتروموتور کمپرسور گاز حفاظت دیفرانسیل 87 اضافه گردد |  | 1401-2294-16105 | 1401-01-20 | رله 87 موتوری در بند 5 از 7 اضافه گردید.
2 | عبارت Avarage حذف گردد. ملاک طراحی تجهیزات الکتریکی مقادیر ماکزیمم و مینیمم می باشد. مطابق مدارک پایه بخش فرآیند ماکزیمم دمای سایه 52 درجه می باشد. لذا مقدار ماکزیمم دما بر این اساس اصلاح گردد. |  | 1401-2294-16105 | 1401-01-20 | عبارت "میانگین" حذف گردید. همچنین دمای ماکزیمم 52 درجه در نظر گرفته شد.
3 | rated Voltage در مدرک برابر 12 کیلوولت در نظر گرفته شود. |  | 1401-2294-16105 | 1401-01-20 | سطح ولتاژ 12 کیلو ولت در نظر گرفته شد.
4 | بند 2.12 به صورت 28، 75 و 2 کیلوولت اصلاح گردد. مقادیر در کل بندهای مشابه اصلاح گردد. |  | 1401-2294-16105 | 1401-01-20 | اصلاح گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozafari | Signature |  |  |  | Clarified By: | Signature
| Date: 16-Mar-2022 |  |  |  |  | Date: